## Rev History
Revision History
Please keep me up to date
Version | Date | Who | Summary of Changes
1 | 2010-04-01 | Bryan Palmintier | Basic Initial Screening Curve Based Capacity Planning. Numbers based on Royal Academy Report
2 | 2010-04-15 | Bryan Palmintier | Implemented Capital Recovery Factor for annualizing capital costs
3 | 2010-04-23 | Bryan Palmintier | Added data for wind
4 | 2010-06 | Bryan Palmintier | Misc updates
5 | 2010-08-01 | Bryan Palmintier | Major overhaul for separate availability and capacity credit (aka Simple Model) to better capture renewables: - Added Availability and Capacity - Converted to EIA data for consistancy with GAMS - Added References Tab - Disaggregated fixed and variable costs - Added carbon emissions & pricing - Compute breakeven hours for wind - increase effective captial costs based on availability de-rating & firming requirements - Converted to *.xls for easier use with the faster Excel 2004 (Mac)
6 | 2010-08-02 09:00 | Bryan Palmintier | Added comments & revision history
7 | 2010-08-02 22:00 | Bryan Palmintier | Cleaned up, improved, and expanded LDC discretization calculation: - moved to separate tab (Discrete LDC) - set non-peak bins to use average values rather than zero-order hold of peak - added adjustmen factor to non-peak bins such that total energy matches reality - corrected minor bin size calculation errors - expanded to 100 max possible bins - structured cells and names for easy further expansion
8 | 2010-09-07 12:52 | Bryan Palmintier | Moved Discrete LDC to separate spreadsheet (with 2009 wind and load data) Updated Load Data to use actual 2009 ERCOT data
9 | 2011-01-22 12:46 | Bryan Palmintier | Added total fixed cost column (not derated)
10 | 2011-07-11 | Bryan Palmintier | Major Overhaul: - Updated cost numbers to use NW Power Plan 2010 Assumptions - Added Automatic calculation of capacity by technology - Added complete cost information - Verified against GAMS & MATLAB models - Updated minor change to demand data (flipped hours)
11 | 2012-01-31 11:46 | Bryan Palmintier | Major Overhaul (again): -- Added lookup table for Gen Data now using EIA 2011 Cost & Heatrate assumptions -- Added CCS support -- Corrected firming cost computations -- Verified with GAMS StaticCapPlan -- Converted to ERCOT2007 demand power series -- Revamped color codes -- Added second mini screen curves for easy interactive use -- Toggle for firming and planning margin computation
12 | 2012-08-28 16:34 | Bryan Palmintier | Modernized to match GAMS models: -- Convert to GW, GWh -- Updated generator assumtions (including new wind capacity factor)
13 | 2013-03-27 01:14 | Bryan Palmintier | Added Extensive Fuel Price Scenarios from AEO2012, with a focus on 2030 & 2035. Also added lookup functionality for cost data by scenario.

## Screening Curves
Renewable Screening Curve Model
Firming cost adjustment based on theoretic work by: Ignacio Perez-Arriaga, Bryan Palmintier, Yuan Yao, & James Merrick | [7 empty] | Color Key:
Input Data
Originally created: | 2010-04-01 | Bryan Palmintier | [5 empty] | Calculated Value
Last updated: | 2013-03-27 01:14 | Bryan Palmintier | [5 empty] | Lookup Value
Intermediate Calculation
System Parameters
WACC | 9% | APR | Use firming cost | TRUE | Demand Hours | 8760
CO2 Price | 0 | /ton CO2e | Use planning margin | TRUE | Peak Demand | 61.99 | MW
Planning Reserve | 13.75% |  | Use Derating | TRUE
|  |  | Derate to Maintenance Weeks | TRUE
Technology Selection |  |  | Fuel Scenario | 2035 AEO2012-LoCoalCost-USA |  | Fuel Scen Index | 60
[5 empty] | Fuel Price | Fuel CO2 | Additional Scaling
Name | Type | Gen index | Fuel | Fuel index | $/MBTU | t Co2e/MBTU | Cap Cost | Fuel Cost
Nuclear | u235_st | 8 | u235 | 1 | 0.64605 | 0 | 1 | 1
Coal | coal_sub_st | 2 | coal | 5 | 1.77 | 0.09552 | 1 | 1
Gas CC | ng_cc | 4 | ng | 4 | 6.78 | 0.05306 | 1 | 1
Gas Peaker | ng_gt_aero | 6 | ng | 4 | 6.78 | 0.05306 | 1 | 1
Wind | wind | 9 | wind | 10 | 0 | 0 | 1 | 1
Coal IGCC+CCS | coal_sub_st_ccs | 11 | coal | 5 | 1.77 | 0.09552 | 1 | 1
NGCC + CCS | ng_cc_ccs | 12 | ng | 4 | 6.78 | 0.05306 | 1 | 1
Insert
[9 empty] | Firm Peaker Cost | 75.1881
[9 empty] | Peaker Idx | 4
Fixed Costs | [8 empty] | Peaker firm/avg | 0.988
| Capital Cost | Life | Capital Recovery | Annual Capital | Fixed O&M | Total Fixed | Availability (derate) | Derated Cost | Capacity Credit | Cost of Firm Cap | Firming Cost | Equiv Fixed
Technology | M$/GW | yr | Factor | M$/GW-yr | M$/GW-yr | M$/GW-yr | annual avg % | M$/GWe-yr | % of rated | M$/Gwpeak-yr | M$/GWe-yr | M$/GWe-yr
Nuclear | 5335 | 30 | 0.097336 | 519.2894 | 88.75 | 608.0394 | 92.31% | 658.7094 | 96% | 633.3744 | -3.9098 | 654.7996
Coal | 2844 | 30 | 0.097336 | 276.8246 | 29.67 | 306.4946 | 90.38% | 339.1004 | 93% | 329.5641 | -3.0779 | 336.0225
Gas CC | 1003 | 30 | 0.097336 | 97.6284 | 14.62 | 112.2484 | 94.23% | 119.1207 | 100% | 112.2484 | -5.5056 | 113.6151
Gas Peaker | 665 | 30 | 0.097336 | 64.7287 | 6.7 | 71.4287 | 96.15% | 74.2858 | 95% | 75.1881 | 0 | 74.2858
Wind | 2438 | 20 | 0.10955 | 267.0743 | 28.07 | 295.1443 | 26.3% | 1122.3749 | 10.5% | 2810.8982 | 44.2637 | 1166.6385
Coal IGCC+CCS | 4579 | 30 | 0.097336 | 445.7032 | 63.21 | 508.9132 | 90.38% | 563.0529 | 93% | 547.2184 | -3.0779 | 559.9749
NGCC + CCS | 2060 | 30 | 0.097336 | 200.5129 | 30.25 | 230.7629 | 94.23% | 244.8912 | 100% | 230.7629 | -5.5056 | 239.3856
Insert
Variable Costs
| Var O&M | Heatrate | Fuel Price | Fuel Cost | Carbon in Fuel | Carbon C&S | Carbon Emit | Carbon Cost | Variable Cost | 8760 Var Cost
| $/MWh | MMBTU/MWh | $/MMBTU | $/MWh | t Co2e/MMBTU | % CO2e | t CO2e/MWh | $/MWh | M$/GWh | M$/8760MWh
Nuclear | 2.04 | 10.4 | 0.64605 | 6.7189 | 0 | 0 | 0 | 0 | 0.0087589 | 76.7278
Coal | 4.25 | 8.8 | 1.77 | 15.576 | 0.09552 | 0 | 0.84058 | 0 | 0.019826 | 173.6758
Gas CC | 3.11 | 6.43 | 6.78 | 43.5954 | 0.05306 | 0 | 0.34118 | 0 | 0.046705 | 409.1393
Gas Peaker | 9.87 | 9.75 | 6.78 | 66.105 | 0.05306 | 0 | 0.51733 | 0 | 0.075975 | 665.541
Wind | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coal IGCC+CCS | 9.05 | 12 | 1.77 | 21.24 | 0.09552 | 0.9 | 0.11462 | 0 | 0.03029 | 265.3404
NGCC + CCS | 6.45 | 7.525 | 6.78 | 51.0195 | 0.05306 | 0.9 | 0.039928 | 0 | 0.05747 | 503.4328
Insert
Breakeven Hours
|  |  | Nuclear | Coal | Gas CC | Gas Peaker | Wind | Coal IGCC+CCS | NGCC + CCS | Insert
|  | fixed | 654.7996 | 336.0225 | 113.6151 | 74.2858 | 1166.6385 | 559.9749 | 239.3856 | 1e+100
| fixed | variable | 0.0087589 | 0.019826 | 0.046705 | 0.075975 | 0 | 0.03029 | 0.05747
Nuclear | 654.7996 | 0.0087589 | - | 28803.9746 | 14261.768 | 8636.5259 | 58436.5928 | 4404.0745 | 8528.2012
Coal | 336.0225 | 0.019826 | 28803.9746 | - | 8274.2687 | 4661.4661 | 41895.292 | -21402.1846 | 2567.1594 | 38.4895 | 74.2858 | 112.7753
Gas CC | 113.6151 | 0.046705 | 14261.768 | 8274.2687 | - | 1343.6904 | 22546.0747 | 27191.5298 | -11684.2574
Gas Peaker | 74.2858 | 0.075975 | 8636.5259 | 4661.4661 | 1343.6904 | - | 14377.7916 | 10631.2601 | 8921.6608
Wind | 1166.6385 | 0 | 58436.5928 | 41895.292 | 22546.0747 | 14377.7916 | - | 20028.511 | 16134.6962
Coal IGCC+CCS | 559.9749 | 0.03029 | 4404.0745 | -21402.1846 | 27191.5298 | 10631.2601 | 20028.511 | - | 11795.262
NGCC + CCS | 239.3856 | 0.05747 | 8528.2012 | 2567.1594 | -11684.2574 | 8921.6608 | 16134.6962 | 11795.262 | -
Sort Segments (iterative sort heuristic for fixed number of iterations)
Note: gens initially reordered by capital cost and then generators are removed one at a time if their var costs too high
Cap Cost Rank | item # |  | Breakeven Hours |  | Check #1 |  |  |  | Check #2 |  |  |  | Check #3 |  |  |  | Check #4 |  |  |  | Check #5 |  |  |  | Check #6
|  | Starting Name List |  | Err Above | New item # | New Names | Breakeven Hr | Err Above | New item # | New Names | Breakeven Hr | Err Above | New item # |  | Breakeven Hr | Err Above | New item # |  | Breakeven Hr | Err Above | New item # |  | Breakeven Hr | Err Above | New item # |  | Breakeven Hr
1 | 4 | Gas Peaker | 0 | 0 | 4 | Gas Peaker | 0 | 0 | 4 | Gas Peaker | 0 | 0 | 4 | Gas Peaker | 0 | 0 | 4 | Gas Peaker | 0 | 0 | 4 | Gas Peaker | 0 | 0 | 4 | Gas Peaker | 0
2 | 3 | Gas CC | 1343.6904 | 0 | 3 | Gas CC | 1343.6904 | 0 | 3 | Gas CC | 1343.6904 | 0 | 3 | Gas CC | 1343.6904 | 0 | 3 | Gas CC | 1343.6904 | 0 | 3 | Gas CC | 1343.6904 | 0 | 3 | Gas CC | 1343.6904
3 | 7 | NGCC + CCS | -11684.2574 | 1 | 2 | Coal | 8274.2687 | 0 | 2 | Coal | 8274.2687 | 0 | 2 | Coal | 8274.2687 | 0 | 2 | Coal | 8274.2687 | 0 | 2 | Coal | 8274.2687 | 0 | 2 | Coal | 8274.2687
4 | 2 | Coal | 2567.1594 | 1 | 6 | Coal IGCC+CCS | 0 | 1 | 1 | Nuclear | 28803.9746 | 1 | 5 | Wind | 41895.292 | 1 |  |  |  | 1 |  |  |  | 1
5 | 6 | Coal IGCC+CCS | -21402.1846 | 1 | 1 | Nuclear | 4404.0745 | 1 | 5 | Wind | 58436.5928 | 1 |  |  |  | 1 |  |  |  | 1 |  |  |  | 1
6 | 1 | Nuclear | 4404.0745 | 1 | 5 | Wind | 58436.5928 | 1 |  |  |  | 1 |  |  |  | 1 |  |  |  | 1 |  |  |  | 1
7 | 5 | Wind | 58436.5928 | 1 |  |  | na | 1 |  |  |  | 1 |  |  |  | 1 |  |  |  | 1 |  |  |  | 1
Insert
Optimal Capacity for Load
| Final item # | Breakeven Hours | Lookup Hour | Power Level | Derated Cap | Uprated Cap
Gas Peaker | 4 | 0 | 1 | 61.99 | 18.396 | 19.1318
Gas CC | 3 | 1343.6904 | 1344 | 43.594 | 18.957 | 20.1176
Coal | 2 | 8274.2687 | 8275 | 24.637 | 24.637 | 27.258
|  |  | 8760 |  | 0
|  |  | 8760 |  | 0
|  |  | 8760 |  | 0
|  |  | 8760 |  | 0
Insert
Energy (GWh) and Emissions
| Cum Cap MW | Cap Constrained | Demand Constrained | Total Energy | Carbon Kton
Gas Peaker | 61.99 | 0 | 6.9214 | 6.9214 | 3.5807
Gas CC | 43.594 | 25.4593 | 59.7812 | 85.2405 | 29.082
Coal | 24.637 | 203.8465 | 11.4465 | 215.293 | 180.9701
| 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
Insert
|  |  |  | 307.4549 | 213.6328
Planning Reserves and total Installed Capacity (GW)
Computer contribution to planning reserves and add peakers as needed to meet demand | [6 empty] | scale 1/ | 5
| Lookup | Uprated Cap for Load | Firm Capacity | Additional Reserve | Total Capacity | Plant Size (GW) | Number of Plants
Nuclear |  |  |  | 0 |  | 1.118 | 0 | 0
Coal | 3 | 27.258 | 25.3499 | 0 | 27.258 | 0.65 | 41.9353 | 8.3871
Gas CC | 2 | 20.1176 | 20.1176 | 0 | 20.1176 | 0.4 | 50.2941 | 10.0588
Gas Peaker | 1 | 19.1318 | 18.1752 | 7.2325 | 26.3643 | 0.21 | 125.5443 | 25.1089
Wind |  |  |  | 0 |  | 0.1 | 0 | 0
Coal IGCC+CCS |  |  |  | 0 |  | 0.65 | 0 | 0
NGCC + CCS |  |  |  | 0 |  | 0.385 | 0 | 0
Insert
|  | Subtotal | 63.6428 |  | 73.7399
|  | Required for Reserves | 70.5136
|  | Additional Cap Required | 6.8708
Costs (in $M)
| Capital | Fixed O&M | Var O&M | Fuel | Carbon | Total
Nuclear | [5 empty] | 0
Coal | 7545.6727 | 808.7436 | 914.9953 | 3353.4038 | 0 | 12622.8153
Gas CC | 1964.0515 | 294.1198 | 265.0979 | 3716.0925 | 0 | 6239.3616
Gas Peaker | 1706.5266 | 176.6409 | 68.3146 | 457.5415 | 0 | 2409.0236
Wind | [5 empty] | 0
Coal IGCC+CCS | [5 empty] | 0
NGCC + CCS | [5 empty] | 0
Insert
Totals | 11216.2508 | 1279.5042 | 1248.4077 | 7527.0378 | 0 | 21271.2006 | OK
Screening Curve Data for Plot
| 0 | 8760
Nuclear | 654.7996 | 731.5274
Coal | 336.0225 | 509.6982
Gas CC | 113.6151 | 522.7544
Gas Peaker | 74.2858 | 739.8268
Wind | 1166.6385 | 1166.6385
Coal IGCC+CCS | 559.9749 | 825.3153
NGCC + CCS | 239.3856 | 742.8184
Note on B5: Bryan Palmintier: DO NOT Enter here… Enter on the Rev History Tab instead
Note on B9: Bryan Palmintier: With Zero carbon cost, 8% will baseload coal and 9% will baseload NGCC Note: ERCOT uses a 9% interest rate, with a 20% equity investment
Note on H34: Bryan Palmintier: Based on ERCOT 2007 actual wind data.

## Raw Gen Data
EIA AEO2011 Generator Cost Assumptions
Notes: | Only includes cost data, additional technical data taken from NW Power Plan above
Source: | US Energy Information Administration [EIA], 2010. Updated Capital Cost Estimates for Electricity Generation Plants (AEO 2011), Washington, DC: US Department of Energy. Available at: http://www.eia.gov/oiaf/beck_plantcosts/.
Cost Basis: | 2010 Dollars
Generator Mapping
| EAI AEO2011 (NEMS) Name |  | NW Power Plan (for non-cost data) |  |  | Note
Coal_ST | Dual Unit Advanced PC |  | Supercritical pulverized coal |  |  | Used only 1/2 capacity b/c we want unit level data
Coal IGCC | Dual Unit Coal IGCC |  | Coal-fired Gasification Combined-cycle |  |  | Used only 1/2 capacity b/c we want unit level data
NG_CC | Advanced NGCC |  | Combined Cycle NG
NG_GT | Advanced CT (F-class) |  | Heavy Duty Frame Gas Turbine
NG_GT_AERO | Advanced CT (F-class) |  | Aeroderivative Gas Turbine
NG_ST | Average of Coal & NGCT |  | Average of Coal & NGCT
U235_ST | Dual Unit Nuclear |  | Gen III+ (Advanced) LWR |  |  | Used only 1/2 capacity b/c we want unit level data
Wind | On-shore Wind
Wind_off | Off-shore Wind
Coal_ST w/ CCS | Dual Unit Advanced PC with CCS |  | Super critical pulverized coal with 90% CCS
NG_CC w/ CCS | Advanced NGCC with CCS |  | Use ratios from coal w/ and w/o CCS applied to CCGT baseline
Coal IGCC w/CCS | Single Unit Coal IGCC |  | Coal-fired Gasification Combined-cycle with CCS |  |  | No double unit data
name
| type | c_var_om | c_fix_om | c_cap | life | heatrate | lead_time | co2_embed | co2_ccs | p_min | cap_credit | gen_size | ramp_max | unit_min_pu | fuel_start | c_start_fix | max_start | quick_start | reg_up | reg_down | spin_rsv | max_cap_fact | derate | min_up | min_down | efor | maint_wks | repair_hr
* | [code] | [$/MWh] | [M$/GW-yr] | [M$/GW] | [yr] | [MMBTU/MWh] | [yr] | [Mt/GW] | [p.u.] | [p.u.] | [p.u.] | [GW] | [p.u./hr] | [p.u.] | [BTUe9/start] | [K$/start] | [start/yr] | [p.u.] | [p.u.] | [p.u.] | [p.u.] | [p.u.] | [p.u.] | [hr] | [hr] | [hr] | [wk/yr] | [hr]
coal_lig_st | coal_lig_st | 4.25 | 29.67 | 2844 | 30 | 8.8 | 7 | 0 | 0 | 0 | 0.93 | 0.65 | 0.3 | 0.5 | 2.6024 | 3.581 | 104 | 0 | 0.025 | 0.025 | 0.05 | 0.85 | 0.85 | 24 | 12 | 0.07 | 5 | 40
coal_sub_st | coal_sub_st | 4.25 | 29.67 | 2844 | 30 | 8.8 | 7 | 0 | 0 | 0 | 0.93 | 0.65 | 0.3 | 0.5 | 2.6024 | 3.581 | 104 | 0 | 0.025 | 0.025 | 0.05 | 0.85 | 0.85 | 24 | 12 | 0.07 | 5 | 40
coal_igcc | coal_igcc | 6.87 | 48.9 | 3221 | 30 | 8.7 | 7 | 0 | 0 | 0 | 0.9 | 0.6 | 0.1 | 0.7 | 2.6024 | 3.581 | 52 | 0 | 0.0083333 | 0.0083333 | 0.016667 | 0.81 | 0.81 | 48 | 24 | 0.1 | 4 | 100
ng_cc | ng_cc | 3.11 | 14.62 | 1003 | 30 | 6.43 | 4.5 | 0 | 0 | 0 | 1 | 0.4 | 1 | 0.3 | 0.58947 | 9.2509 | 365 | 0 | 0.083333 | 0.083333 | 0.16667 | 0.89 | 0.89 | 6 | 12 | 0.06 | 3 | 32
ng_gt | ng_gt | 9.87 | 6.7 | 665 | 30 | 9.75 | 2.75 | 0 | 0 | 0 | 0.95 | 0.21 | 6 | 0.25 | 0.18772 | 7.8112 | Inf | 0 | 0.5 | 0.5 | 1 | 0.91 | 0.91 | 0 | 0 | 0.05 | 2 | 88
ng_gt_aero | ng_gt_aero | 9.87 | 6.7 | 665 | 30 | 9.75 | 2.75 | 0 | 0 | 0 | 0.95 | 0.21 | 6 | 0.25 | 0 | 1 | Inf | 1 | 0.5 | 0.5 | 1 | 0.91 | 0.91 | 0 | 0 | 0.05 | 2 | 88
ng_st | ng_st | 3.68 | 22.145 | 1923.5 | 30 | 8.8 | 5.75 | 0 | 0 | 0 | 0.965 | 0.31 | 0.3 | 0.5 | 2.6024 | 3.581 | 52 | 0 | 0.025 | 0.025 | 0.05 | 0.85 | 0.85 | 24 | 12 | 0.07 | 5 | 40
u235_st | u235_st | 2.04 | 88.75 | 5335 | 30 | 10.4 | 10 | 0 | 0 | 0 | 0.96 | 1.118 | 0.1 | 0.8 | 0 | 100 | 1 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 48 | 24 | 0.042 | 4 | 112
wind | wind | 0 | 28.07 | 2438 | 20 | 1 | 4.5 | 0 | 0 | 0 | 0.105 | 0.1 | 1 | 0 | 0 | 0 | Inf | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0
pv_util | pv_util | 0 | 16.7 | 4755 | 25 | 1 | 3 | 0 | 0 | 0 | 0.6 | 0.15 | 1 | 0 | 0 | 0 | Inf | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0
coal_sub_st_ccs | coal_sub_st_ccs | 9.05 | 63.21 | 4579 | 30 | 12 | 9 | 0 | 0.9 | 0 | 0.93 | 0.65 | 0.3 | 0.5 | 2.6024 | 3.581 | 52 | 0 | 0.025 | 0.025 | 0.05 | 0.85 | 0.85 | 24 | 12 | 0.07 | 5 | 40
ng_cc_ccs | ng_cc_ccs | 6.45 | 30.25 | 2060 | 30 | 7.525 | 5.7857 | 0 | 0.9 | 0 | 1 | 0.385 | 1 | 0.3 | 0.58947 | 9.2509 | 365 | 0 | 0.083333 | 0.083333 | 0.16667 | 0.89 | 0.89 | 6 | 12 | 0.06 | 3 | 32
coal_igcc_ccs | coal_igcc_ccs | 8.04 | 69.3 | 5348 | 30 | 10.7 | 9 | 0 | 0.88 | 0 | 0.9 | 0.52 | 0.1 | 0.7 | 2.6024 | 3.581 | 52 | 0 | 0.0083333 | 0.0083333 | 0.016667 | 0.81 | 0.81 | 48 | 24 | 0.1 | 4 | 100
wind_off | wind_off | 0 | 53.33 | 5975 | 20 | 1 | 6 | 0 | 0 | 0 | 0.105 | 0.4 | 1 | 0 | 0 | 0 | Inf | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0
pv_dist | pv_dist | 0 | 26.04 | 6050 | 25 | 1 | 3 | 0 | 0 | 0 | 0.6 | 0.007 | 1 | 0 | 0 | 0 | Inf | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Insert Spacer | Insert Spacer
Note on G30: Bryan Palmintier: Assumed equal to coal steam
Note on M30: Bryan Palmintier: Average unit size for NG steam in ERCOT
Note on G31: Bryan Palmintier: Not specified in AEO. Use 10.4which implies 33% thermal efficiency
Note on A33: Bryan Palmintier: Note: no offshore wind data in Northwest Power Plan data
Note on F33: Bryan Palmintier: Set equal to on-shore wind
Note on H33: Bryan Palmintier: Manual change to recognize longer lead times for off-shore
Note on I33: Bryan Palmintier: Set equal to on-shore wind
Note on J33: Bryan Palmintier: Set equal to on-shore wind
Note on K33: Bryan Palmintier: Set equal to on-shore wind
Note on L33: Bryan Palmintier: Set equal to on-shore wind
Note on N33: Bryan Palmintier: Set equal to on-shore wind
Note on O33: Bryan Palmintier: Set equal to on-shore wind
Note on P33: Bryan Palmintier: Set equal to on-shore wind
Note on Q33: Bryan Palmintier: Set equal to on-shore wind
Note on R33: Bryan Palmintier: Set equal to on-shore wind
Note on S33: Bryan Palmintier: Set equal to on-shore wind
Note on T33: Bryan Palmintier: Set equal to on-shore wind
Note on U33: Bryan Palmintier: Set equal to on-shore wind
Note on V33: Bryan Palmintier: Set equal to on-shore wind
Note on W33: Bryan Palmintier: Set equal to on-shore wind
Note on X33: Bryan Palmintier: Set equal to on-shore wind
Note on Y33: Bryan Palmintier: Set equal to on-shore wind
Note on Z33: Bryan Palmintier: Set equal to on-shore wind

## Raw Load Data
ERCOT 2007 Load Data
Sorted Highest to lowest for load duration curves
Demand (GW)
1 | 61.99
2 | 61.919
3 | 61.417
4 | 61.355
5 | 61.209
6 | 60.851
7 | 60.694
8 | 60.349
9 | 60.345
10 | 59.286
11 | 59.217
12 | 59.048
13 | 58.972
14 | 58.964
15 | 58.911
16 | 58.812
17 | 58.733
18 | 58.71
19 | 58.484
20 | 58.45
21 | 58.433
22 | 58.395
23 | 58.313
24 | 58.296
25 | 58.265
26 | 58.234
27 | 58.214
28 | 58.126
29 | 58.101
30 | 58.034
31 | 57.964
32 | 57.928
33 | 57.927
34 | 57.926
35 | 57.907
36 | 57.858
37 | 57.807
38 | 57.784
39 | 57.698
40 | 57.685
41 | 57.558
42 | 57.556
43 | 57.538
44 | 57.522
45 | 57.444
46 | 57.414
47 | 57.304
48 | 57.292
49 | 57.158
50 | 57.122
51 | 57.064
52 | 57.041
53 | 56.959
54 | 56.949
55 | 56.929
56 | 56.894
57 | 56.769
58 | 56.71
59 | 56.669
60 | 56.584
61 | 56.552
62 | 56.551
63 | 56.465
64 | 56.447
65 | 56.351
66 | 56.332
67 | 56.315
68 | 56.283
69 | 56.261
70 | 56.206
71 | 56.195
72 | 56.132
73 | 56.085
74 | 56.026
75 | 56.014
76 | 55.991
77 | 55.978
78 | 55.944
79 | 55.845
80 | 55.84
81 | 55.839
82 | 55.821
83 | 55.821
84 | 55.756
85 | 55.726
86 | 55.697
87 | 55.653
88 | 55.635
89 | 55.589
90 | 55.571
91 | 55.542
92 | 55.512
93 | 55.487
94 | 55.469
95 | 55.425
96 | 55.424
97 | 55.404
98 | 55.349
99 | 55.326
100 | 55.281
101 | 55.233
102 | 55.2
103 | 55.193
104 | 55.131
105 | 55.092
106 | 55.091
107 | 55.045
108 | 55.044
109 | 54.983
110 | 54.933
111 | 54.904
112 | 54.889
113 | 54.889
114 | 54.772
115 | 54.766
116 | 54.731
117 | 54.683
118 | 54.683
119 | 54.667
120 | 54.656
121 | 54.594
122 | 54.579
123 | 54.567
124 | 54.56
125 | 54.554
126 | 54.436
127 | 54.409
128 | 54.331
129 | 54.324
130 | 54.296
131 | 54.246
132 | 54.244
133 | 54.22
134 | 54.204
135 | 54.195
136 | 54.188
137 | 54.18
138 | 54.167
139 | 54.161
140 | 54.138
141 | 54.122
142 | 54.078
143 | 54.053
144 | 54.043
145 | 53.975
146 | 53.948
147 | 53.922
148 | 53.908
149 | 53.888
150 | 53.876
151 | 53.87
152 | 53.867
153 | 53.834
154 | 53.796
155 | 53.756
156 | 53.755
157 | 53.745
158 | 53.735
159 | 53.714
160 | 53.708
161 | 53.698
162 | 53.69
163 | 53.688
164 | 53.678
165 | 53.674
166 | 53.605
167 | 53.603
168 | 53.587
169 | 53.583
170 | 53.576
171 | 53.57
172 | 53.52
173 | 53.512
174 | 53.491
175 | 53.463
176 | 53.461
177 | 53.448
178 | 53.417
179 | 53.405
180 | 53.38
181 | 53.328
182 | 53.323
183 | 53.312
184 | 53.271
185 | 53.243
186 | 53.193
187 | 53.166
188 | 53.152
189 | 53.141
190 | 53.111
191 | 53.108
192 | 53.103
193 | 53.084
194 | 53.066
195 | 53.059
196 | 53.04
197 | 53.026
198 | 53.024
199 | 53.005
200 | 52.976
201 | 52.965
202 | 52.965
203 | 52.962
204 | 52.959
205 | 52.957
206 | 52.919
207 | 52.879
208 | 52.853
209 | 52.834
210 | 52.834
211 | 52.822
212 | 52.814
213 | 52.804
214 | 52.801
215 | 52.797
216 | 52.789
217 | 52.767
218 | 52.722
219 | 52.702
220 | 52.689
221 | 52.679
222 | 52.664
223 | 52.606
224 | 52.574
225 | 52.568
226 | 52.548
227 | 52.545
228 | 52.535
229 | 52.507
230 | 52.451
231 | 52.447
232 | 52.447
233 | 52.446
234 | 52.435
235 | 52.432
236 | 52.426
237 | 52.425
238 | 52.384
239 | 52.374
240 | 52.368
241 | 52.363
242 | 52.337
243 | 52.314
244 | 52.301
245 | 52.3
246 | 52.297
247 | 52.29
248 | 52.234
249 | 52.223
250 | 52.213
251 | 52.213
252 | 52.209
253 | 52.208
254 | 52.202
255 | 52.201
256 | 52.194
257 | 52.188
258 | 52.186
259 | 52.184
260 | 52.172
261 | 52.164
262 | 52.149
263 | 52.144
264 | 52.106
265 | 52.086
266 | 52.079
267 | 52.077
268 | 52.034
269 | 52.021
270 | 52.015
271 | 52.002
272 | 51.988
273 | 51.962
274 | 51.921
275 | 51.913
276 | 51.909
277 | 51.903
278 | 51.891
279 | 51.868
280 | 51.843
281 | 51.834
282 | 51.826
283 | 51.79
284 | 51.782
285 | 51.779
286 | 51.767
287 | 51.764
288 | 51.759
289 | 51.72
290 | 51.718
291 | 51.705
292 | 51.695
293 | 51.685
294 | 51.668
295 | 51.623
296 | 51.622
297 | 51.61
298 | 51.592
299 | 51.579
300 | 51.523
301 | 51.506
302 | 51.478
303 | 51.466
304 | 51.458
305 | 51.449
306 | 51.444
307 | 51.438
308 | 51.417
309 | 51.413
310 | 51.409
311 | 51.403
312 | 51.4
313 | 51.392
314 | 51.39
315 | 51.37
316 | 51.355
317 | 51.351
318 | 51.349
319 | 51.344
320 | 51.342
321 | 51.335
322 | 51.334
323 | 51.325
324 | 51.319
325 | 51.31
326 | 51.298
327 | 51.294
328 | 51.283
329 | 51.253
330 | 51.252
331 | 51.213
332 | 51.206
333 | 51.205
334 | 51.202
335 | 51.197
336 | 51.184
337 | 51.178
338 | 51.174
339 | 51.125
340 | 51.121
341 | 51.108
342 | 51.095
343 | 51.093
344 | 51.086
345 | 51.064
346 | 51.041
347 | 51.038
348 | 51.037
349 | 51.022
350 | 51.016
351 | 51.012
352 | 51.006
353 | 50.995
354 | 50.991
355 | 50.983
356 | 50.964
357 | 50.963
358 | 50.961
359 | 50.954
360 | 50.953
361 | 50.946
362 | 50.937
363 | 50.932
364 | 50.91
365 | 50.896
366 | 50.88
367 | 50.858
368 | 50.854
369 | 50.85
370 | 50.845
371 | 50.824
372 | 50.815
373 | 50.778
374 | 50.766
375 | 50.73
376 | 50.724
377 | 50.72
378 | 50.677
379 | 50.662
380 | 50.643
381 | 50.642
382 | 50.637
383 | 50.632
384 | 50.627
385 | 50.627
386 | 50.614
387 | 50.601
388 | 50.598
389 | 50.595
390 | 50.586
391 | 50.586
392 | 50.565
393 | 50.558
394 | 50.554
395 | 50.548
396 | 50.53
397 | 50.528
398 | 50.516
399 | 50.515
400 | 50.513
401 | 50.512
402 | 50.491
403 | 50.481
404 | 50.478
405 | 50.472
406 | 50.446
407 | 50.422
408 | 50.409
409 | 50.408
410 | 50.403
411 | 50.392
412 | 50.388
413 | 50.375
414 | 50.373
415 | 50.357
416 | 50.348
417 | 50.345
418 | 50.319
419 | 50.305
420 | 50.302
421 | 50.287
422 | 50.284
423 | 50.272
424 | 50.245
425 | 50.237
426 | 50.233
427 | 50.221
428 | 50.214
429 | 50.213
430 | 50.212
431 | 50.208
432 | 50.208
433 | 50.18
434 | 50.146
435 | 50.143
436 | 50.12
437 | 50.119
438 | 50.112
439 | 50.087
440 | 50.082
441 | 50.073
442 | 50.058
443 | 50.03
444 | 50.019
445 | 50.01
446 | 50.001
447 | 49.986
448 | 49.985
449 | 49.978
450 | 49.974
451 | 49.951
452 | 49.931
453 | 49.917
454 | 49.917
455 | 49.897
456 | 49.883
457 | 49.867
458 | 49.861
459 | 49.843
460 | 49.822
461 | 49.803
462 | 49.775
463 | 49.769
464 | 49.748
465 | 49.741
466 | 49.735
467 | 49.722
468 | 49.709
469 | 49.699
470 | 49.69
471 | 49.686
472 | 49.651
473 | 49.651
474 | 49.648
475 | 49.644
476 | 49.605
477 | 49.586
478 | 49.582
479 | 49.574
480 | 49.573
481 | 49.567
482 | 49.554
483 | 49.544
484 | 49.543
485 | 49.536
486 | 49.523
487 | 49.511
488 | 49.481
489 | 49.479
490 | 49.468
491 | 49.458
492 | 49.45
493 | 49.439
494 | 49.429
495 | 49.421
496 | 49.396
497 | 49.39
498 | 49.383
499 | 49.382
500 | 49.369
501 | 49.353
502 | 49.35
503 | 49.334
504 | 49.316
505 | 49.297
506 | 49.294
507 | 49.286
508 | 49.284
509 | 49.268
510 | 49.266
511 | 49.264
512 | 49.262
513 | 49.25
514 | 49.238
515 | 49.235
516 | 49.189
517 | 49.18
518 | 49.179
519 | 49.163
520 | 49.152
521 | 49.148
522 | 49.136
523 | 49.135
524 | 49.116
525 | 49.101
526 | 49.091
527 | 49.091
528 | 49.068
529 | 49.068
530 | 49.06
531 | 49.057
532 | 49.046
533 | 49.043
534 | 49.034
535 | 49.03
536 | 49.026
537 | 49.016
538 | 49.011
539 | 49.009
540 | 49.001
541 | 48.997
542 | 48.996
543 | 48.978
544 | 48.977
545 | 48.976
546 | 48.971
547 | 48.949
548 | 48.946
549 | 48.93
550 | 48.926
551 | 48.923
552 | 48.919
553 | 48.889
554 | 48.876
555 | 48.874
556 | 48.862
557 | 48.854
558 | 48.851
559 | 48.835
560 | 48.829
561 | 48.828
562 | 48.826
563 | 48.82
564 | 48.819
565 | 48.808
566 | 48.807
567 | 48.801
568 | 48.8
569 | 48.757
570 | 48.747
571 | 48.738
572 | 48.729
573 | 48.718
574 | 48.715
575 | 48.715
576 | 48.709
577 | 48.696
578 | 48.69
579 | 48.686
580 | 48.674
581 | 48.673
582 | 48.672
583 | 48.67
584 | 48.665
585 | 48.659
586 | 48.656
587 | 48.656
588 | 48.645
589 | 48.629
590 | 48.618
591 | 48.616
592 | 48.605
593 | 48.586
594 | 48.584
595 | 48.558
596 | 48.555
597 | 48.553
598 | 48.549
599 | 48.548
600 | 48.546
601 | 48.534
602 | 48.529
603 | 48.529
604 | 48.527
605 | 48.521
606 | 48.51
607 | 48.507
608 | 48.5
609 | 48.499
610 | 48.493
611 | 48.488
612 | 48.485
613 | 48.483
614 | 48.481
615 | 48.473
616 | 48.461
617 | 48.461
618 | 48.44
619 | 48.434
620 | 48.429
621 | 48.42
622 | 48.404
623 | 48.403
624 | 48.401
625 | 48.399
626 | 48.388
627 | 48.383
628 | 48.369
629 | 48.359
630 | 48.357
631 | 48.35
632 | 48.349
633 | 48.346
634 | 48.341
635 | 48.329
636 | 48.322
637 | 48.321
638 | 48.284
639 | 48.267
640 | 48.263
641 | 48.262
642 | 48.244
643 | 48.243
644 | 48.219
645 | 48.217
646 | 48.205
647 | 48.198
648 | 48.19
649 | 48.188
650 | 48.18
651 | 48.172
652 | 48.17
653 | 48.169
654 | 48.147
655 | 48.145
656 | 48.142
657 | 48.14
658 | 48.129
659 | 48.128
660 | 48.107
661 | 48.1
662 | 48.089
663 | 48.08
664 | 48.075
665 | 48.074
666 | 48.06
667 | 48.049
668 | 48.041
669 | 48.039
670 | 48.021
671 | 48.016
672 | 48.012
673 | 48.004
674 | 47.999
675 | 47.992
676 | 47.991
677 | 47.981
678 | 47.979
679 | 47.972
680 | 47.967
681 | 47.953
682 | 47.936
683 | 47.928
684 | 47.927
685 | 47.918
686 | 47.914
687 | 47.899
688 | 47.888
689 | 47.877
690 | 47.877
691 | 47.872
692 | 47.871
693 | 47.866
694 | 47.853
695 | 47.815
696 | 47.814
697 | 47.804
698 | 47.803
699 | 47.799
700 | 47.799
701 | 47.796
702 | 47.783
703 | 47.773
704 | 47.758
705 | 47.753
706 | 47.73
707 | 47.721
708 | 47.719
709 | 47.704
710 | 47.7
711 | 47.7
712 | 47.691
713 | 47.689
714 | 47.688
715 | 47.688
716 | 47.687
717 | 47.657
718 | 47.639
719 | 47.639
720 | 47.633
721 | 47.631
722 | 47.631
723 | 47.627
724 | 47.606
725 | 47.599
726 | 47.594
727 | 47.589
728 | 47.585
729 | 47.567
730 | 47.567
731 | 47.557
732 | 47.554
733 | 47.554
734 | 47.551
735 | 47.537
736 | 47.531
737 | 47.523
738 | 47.518
739 | 47.514
740 | 47.512
741 | 47.495
742 | 47.493
743 | 47.492
744 | 47.483
745 | 47.481
746 | 47.477
747 | 47.469
748 | 47.468
749 | 47.453
750 | 47.434
751 | 47.383
752 | 47.381
753 | 47.377
754 | 47.374
755 | 47.363
756 | 47.363
757 | 47.318
758 | 47.313
759 | 47.303
760 | 47.296
761 | 47.291
762 | 47.288
763 | 47.287
764 | 47.283
765 | 47.281
766 | 47.28
767 | 47.273
768 | 47.27
769 | 47.254
770 | 47.228
771 | 47.226
772 | 47.224
773 | 47.209
774 | 47.2
775 | 47.2
776 | 47.192
777 | 47.186
778 | 47.177
779 | 47.174
780 | 47.167
781 | 47.166
782 | 47.156
783 | 47.11
784 | 47.095
785 | 47.081
786 | 47.08
787 | 47.079
788 | 47.063
789 | 47.063
790 | 47.063
791 | 47.062
792 | 47.06
793 | 47.057
794 | 47.054
795 | 47.054
796 | 47.053
797 | 47.05
798 | 47.049
799 | 47.045
800 | 47.041
801 | 47.036
802 | 47.032
803 | 47.023
804 | 46.996
805 | 46.99
806 | 46.983
807 | 46.96
808 | 46.958
809 | 46.949
810 | 46.948
811 | 46.946
812 | 46.937
813 | 46.935
814 | 46.918
815 | 46.902
816 | 46.894
817 | 46.893
818 | 46.89
819 | 46.887
820 | 46.88
821 | 46.869
822 | 46.839
823 | 46.835
824 | 46.831
825 | 46.811
826 | 46.803
827 | 46.797
828 | 46.791
829 | 46.791
830 | 46.787
831 | 46.78
832 | 46.776
833 | 46.773
834 | 46.767
835 | 46.765
836 | 46.763
837 | 46.76
838 | 46.749
839 | 46.728
840 | 46.707
841 | 46.699
842 | 46.694
843 | 46.692
844 | 46.687
845 | 46.674
846 | 46.668
847 | 46.662
848 | 46.66
849 | 46.656
850 | 46.653
851 | 46.651
852 | 46.65
853 | 46.638
854 | 46.638
855 | 46.632
856 | 46.621
857 | 46.606
858 | 46.603
859 | 46.598
860 | 46.581
861 | 46.575
862 | 46.571
863 | 46.571
864 | 46.564
865 | 46.556
866 | 46.548
867 | 46.543
868 | 46.539
869 | 46.535
870 | 46.516
871 | 46.509
872 | 46.506
873 | 46.494
874 | 46.485
875 | 46.483
876 | 46.477
877 | 46.467
878 | 46.43
879 | 46.415
880 | 46.411
881 | 46.408
882 | 46.405
883 | 46.402
884 | 46.397
885 | 46.397
886 | 46.395
887 | 46.388
888 | 46.376
889 | 46.372
890 | 46.37
891 | 46.369
892 | 46.362
893 | 46.354
894 | 46.341
895 | 46.328
896 | 46.326
897 | 46.322
898 | 46.322
899 | 46.32
900 | 46.318
901 | 46.311
902 | 46.292
903 | 46.291
904 | 46.282
905 | 46.279
906 | 46.269
907 | 46.269
908 | 46.268
909 | 46.263
910 | 46.258
911 | 46.233
912 | 46.22
913 | 46.212
914 | 46.212
915 | 46.205
916 | 46.196
917 | 46.173
918 | 46.167
919 | 46.161
920 | 46.156
921 | 46.138
922 | 46.134
923 | 46.131
924 | 46.125
925 | 46.124
926 | 46.117
927 | 46.11
928 | 46.101
929 | 46.1
930 | 46.1
931 | 46.097
932 | 46.092
933 | 46.091
934 | 46.082
935 | 46.074
936 | 46.074
937 | 46.071
938 | 46.063
939 | 46.054
940 | 46.043
941 | 46.042
942 | 46.023
943 | 46.022
944 | 46.021
945 | 46.02
946 | 46.017
947 | 46.015
948 | 46.013
949 | 46.009
950 | 46.003
951 | 46.003
952 | 45.994
953 | 45.985
954 | 45.973
955 | 45.968
956 | 45.966
957 | 45.952
958 | 45.942
959 | 45.94
960 | 45.93
961 | 45.921
962 | 45.919
963 | 45.917
964 | 45.904
965 | 45.896
966 | 45.895
967 | 45.884
968 | 45.85
969 | 45.848
970 | 45.847
971 | 45.842
972 | 45.841
973 | 45.839
974 | 45.837
975 | 45.829
976 | 45.8
977 | 45.788
978 | 45.78
979 | 45.774
980 | 45.769
981 | 45.764
982 | 45.763
983 | 45.736
984 | 45.734
985 | 45.732
986 | 45.717
987 | 45.707
988 | 45.696
989 | 45.674
990 | 45.674
991 | 45.671
992 | 45.669
993 | 45.669
994 | 45.659
995 | 45.658
996 | 45.653
997 | 45.637
998 | 45.627
999 | 45.622
1000 | 45.621
1001 | 45.62
1002 | 45.61
1003 | 45.597
1004 | 45.593
1005 | 45.593
1006 | 45.58
1007 | 45.563
1008 | 45.556
1009 | 45.554
1010 | 45.547
1011 | 45.542
1012 | 45.537
1013 | 45.53
1014 | 45.519
1015 | 45.518
1016 | 45.513
1017 | 45.507
1018 | 45.503
1019 | 45.502
1020 | 45.501
1021 | 45.485
1022 | 45.483
1023 | 45.475
1024 | 45.473
1025 | 45.471
1026 | 45.469
1027 | 45.469
1028 | 45.463
1029 | 45.461
1030 | 45.454
1031 | 45.45
1032 | 45.447
1033 | 45.432
1034 | 45.42
1035 | 45.414
1036 | 45.41
1037 | 45.404
1038 | 45.373
1039 | 45.368
1040 | 45.364
1041 | 45.346
1042 | 45.336
1043 | 45.333
1044 | 45.327
1045 | 45.315
1046 | 45.313
1047 | 45.312
1048 | 45.308
1049 | 45.308
1050 | 45.304
1051 | 45.303
1052 | 45.291
1053 | 45.291
1054 | 45.29
1055 | 45.28
1056 | 45.27
1057 | 45.27
1058 | 45.264
1059 | 45.25
1060 | 45.245
1061 | 45.244
1062 | 45.237
1063 | 45.236
1064 | 45.231
1065 | 45.231
1066 | 45.226
1067 | 45.219
1068 | 45.212
1069 | 45.21
1070 | 45.202
1071 | 45.2
1072 | 45.193
1073 | 45.187
1074 | 45.187
1075 | 45.179
1076 | 45.164
1077 | 45.164
1078 | 45.162
1079 | 45.16
1080 | 45.156
1081 | 45.156
1082 | 45.154
1083 | 45.153
1084 | 45.146
1085 | 45.135
1086 | 45.134
1087 | 45.126
1088 | 45.123
1089 | 45.121
1090 | 45.12
1091 | 45.12
1092 | 45.115
1093 | 45.113
1094 | 45.11
1095 | 45.109
1096 | 45.098
1097 | 45.089
1098 | 45.086
1099 | 45.086
1100 | 45.075
1101 | 45.062
1102 | 45.041
1103 | 45.03
1104 | 45.025
1105 | 45.014
1106 | 45.008
1107 | 45.003
1108 | 45.003
1109 | 45
1110 | 44.988
1111 | 44.975
1112 | 44.973
1113 | 44.969
1114 | 44.969
1115 | 44.968
1116 | 44.964
1117 | 44.962
1118 | 44.959
1119 | 44.95
1120 | 44.942
1121 | 44.937
1122 | 44.923
1123 | 44.921
1124 | 44.92
1125 | 44.913
1126 | 44.911
1127 | 44.911
1128 | 44.901
1129 | 44.893
1130 | 44.891
1131 | 44.877
1132 | 44.858
1133 | 44.858
1134 | 44.855
1135 | 44.854
1136 | 44.851
1137 | 44.847
1138 | 44.841
1139 | 44.839
1140 | 44.833
1141 | 44.828
1142 | 44.826
1143 | 44.826
1144 | 44.809
1145 | 44.803
1146 | 44.791
1147 | 44.788
1148 | 44.781
1149 | 44.775
1150 | 44.773
1151 | 44.771
1152 | 44.771
1153 | 44.769
1154 | 44.762
1155 | 44.741
1156 | 44.74
1157 | 44.739
1158 | 44.733
1159 | 44.729
1160 | 44.718
1161 | 44.715
1162 | 44.703
1163 | 44.698
1164 | 44.695
1165 | 44.694
1166 | 44.68
1167 | 44.666
1168 | 44.656
1169 | 44.649
1170 | 44.639
1171 | 44.636
1172 | 44.617
1173 | 44.613
1174 | 44.609
1175 | 44.605
1176 | 44.603
1177 | 44.601
1178 | 44.599
1179 | 44.598
1180 | 44.584
1181 | 44.576
1182 | 44.573
1183 | 44.57
1184 | 44.57
1185 | 44.564
1186 | 44.529
1187 | 44.509
1188 | 44.506
1189 | 44.504
1190 | 44.504
1191 | 44.501
1192 | 44.501
1193 | 44.496
1194 | 44.494
1195 | 44.493
1196 | 44.489
1197 | 44.487
1198 | 44.48
1199 | 44.459
1200 | 44.452
1201 | 44.451
1202 | 44.45
1203 | 44.442
1204 | 44.431
1205 | 44.431
1206 | 44.431
1207 | 44.414
1208 | 44.414
1209 | 44.413
1210 | 44.406
1211 | 44.405
1212 | 44.398
1213 | 44.397
1214 | 44.395
1215 | 44.378
1216 | 44.375
1217 | 44.365
1218 | 44.355
1219 | 44.351
1220 | 44.345
1221 | 44.344
1222 | 44.344
1223 | 44.329
1224 | 44.328
1225 | 44.325
1226 | 44.319
1227 | 44.315
1228 | 44.305
1229 | 44.302
1230 | 44.296
1231 | 44.288
1232 | 44.284
1233 | 44.27
1234 | 44.264
1235 | 44.26
1236 | 44.247
1237 | 44.243
1238 | 44.241
1239 | 44.239
1240 | 44.229
1241 | 44.219
1242 | 44.218
1243 | 44.215
1244 | 44.204
1245 | 44.188
1246 | 44.185
1247 | 44.178
1248 | 44.17
1249 | 44.162
1250 | 44.152
1251 | 44.147
1252 | 44.141
1253 | 44.14
1254 | 44.139
1255 | 44.132
1256 | 44.126
1257 | 44.121
1258 | 44.116
1259 | 44.102
1260 | 44.102
1261 | 44.099
1262 | 44.098
1263 | 44.091
1264 | 44.08
1265 | 44.069
1266 | 44.057
1267 | 44.045
1268 | 44.042
1269 | 44.036
1270 | 44.022
1271 | 44.018
1272 | 44.007
1273 | 44.003
1274 | 44
1275 | 43.997
1276 | 43.99
1277 | 43.986
1278 | 43.985
1279 | 43.982
1280 | 43.958
1281 | 43.955
1282 | 43.952
1283 | 43.949
1284 | 43.946
1285 | 43.94
1286 | 43.926
1287 | 43.926
1288 | 43.919
1289 | 43.911
1290 | 43.903
1291 | 43.889
1292 | 43.875
1293 | 43.857
1294 | 43.852
1295 | 43.843
1296 | 43.828
1297 | 43.823
1298 | 43.822
1299 | 43.807
1300 | 43.805
1301 | 43.804
1302 | 43.794
1303 | 43.781
1304 | 43.78
1305 | 43.778
1306 | 43.776
1307 | 43.773
1308 | 43.769
1309 | 43.76
1310 | 43.749
1311 | 43.748
1312 | 43.743
1313 | 43.736
1314 | 43.731
1315 | 43.726
1316 | 43.704
1317 | 43.704
1318 | 43.699
1319 | 43.695
1320 | 43.69
1321 | 43.686
1322 | 43.684
1323 | 43.683
1324 | 43.681
1325 | 43.68
1326 | 43.677
1327 | 43.674
1328 | 43.674
1329 | 43.661
1330 | 43.65
1331 | 43.643
1332 | 43.641
1333 | 43.635
1334 | 43.635
1335 | 43.633
1336 | 43.629
1337 | 43.629
1338 | 43.618
1339 | 43.61
1340 | 43.606
1341 | 43.606
1342 | 43.598
1343 | 43.596
1344 | 43.594
1345 | 43.59
1346 | 43.582
1347 | 43.573
1348 | 43.567
1349 | 43.564
1350 | 43.552
1351 | 43.544
1352 | 43.536
1353 | 43.526
1354 | 43.507
1355 | 43.505
1356 | 43.482
1357 | 43.461
1358 | 43.441
1359 | 43.437
1360 | 43.429
1361 | 43.428
1362 | 43.41
1363 | 43.402
1364 | 43.396
1365 | 43.394
1366 | 43.39
1367 | 43.388
1368 | 43.379
1369 | 43.377
1370 | 43.365
1371 | 43.364
1372 | 43.363
1373 | 43.363
1374 | 43.349
1375 | 43.343
1376 | 43.336
1377 | 43.333
1378 | 43.33
1379 | 43.329
1380 | 43.326
1381 | 43.321
1382 | 43.321
1383 | 43.32
1384 | 43.315
1385 | 43.305
1386 | 43.303
1387 | 43.286
1388 | 43.286
1389 | 43.264
1390 | 43.25
1391 | 43.243
1392 | 43.241
1393 | 43.239
1394 | 43.239
1395 | 43.239
1396 | 43.239
1397 | 43.234
1398 | 43.23
1399 | 43.226
1400 | 43.219
1401 | 43.207
1402 | 43.206
1403 | 43.192
1404 | 43.175
1405 | 43.158
1406 | 43.157
1407 | 43.15
1408 | 43.14
1409 | 43.138
1410 | 43.135
1411 | 43.134
1412 | 43.115
1413 | 43.113
1414 | 43.11
1415 | 43.098
1416 | 43.091
1417 | 43.09
1418 | 43.084
1419 | 43.076
1420 | 43.076
1421 | 43.075
1422 | 43.071
1423 | 43.032
1424 | 42.996
1425 | 42.995
1426 | 42.993
1427 | 42.986
1428 | 42.977
1429 | 42.961
1430 | 42.96
1431 | 42.956
1432 | 42.946
1433 | 42.941
1434 | 42.938
1435 | 42.936
1436 | 42.929
1437 | 42.929
1438 | 42.916
1439 | 42.914
1440 | 42.907
1441 | 42.903
1442 | 42.9
1443 | 42.89
1444 | 42.881
1445 | 42.881
1446 | 42.876
1447 | 42.866
1448 | 42.866
1449 | 42.865
1450 | 42.861
1451 | 42.859
1452 | 42.856
1453 | 42.853
1454 | 42.846
1455 | 42.84
1456 | 42.837
1457 | 42.836
1458 | 42.833
1459 | 42.828
1460 | 42.822
1461 | 42.819
1462 | 42.818
1463 | 42.809
1464 | 42.807
1465 | 42.805
1466 | 42.801
1467 | 42.796
1468 | 42.788
1469 | 42.785
1470 | 42.781
1471 | 42.78
1472 | 42.777
1473 | 42.758
1474 | 42.747
1475 | 42.737
1476 | 42.728
1477 | 42.716
1478 | 42.715
1479 | 42.709
1480 | 42.704
1481 | 42.701
1482 | 42.698
1483 | 42.698
1484 | 42.697
1485 | 42.686
1486 | 42.685
1487 | 42.682
1488 | 42.67
1489 | 42.649
1490 | 42.641
1491 | 42.619
1492 | 42.618
1493 | 42.614
1494 | 42.613
1495 | 42.611
1496 | 42.607
1497 | 42.604
1498 | 42.596
1499 | 42.582
1500 | 42.58
1501 | 42.578
1502 | 42.577
1503 | 42.573
1504 | 42.56
1505 | 42.558
1506 | 42.552
1507 | 42.552
1508 | 42.546
1509 | 42.546
1510 | 42.541
1511 | 42.536
1512 | 42.534
1513 | 42.531
1514 | 42.53
1515 | 42.526
1516 | 42.519
1517 | 42.516
1518 | 42.515
1519 | 42.515
1520 | 42.508
1521 | 42.503
1522 | 42.497
1523 | 42.496
1524 | 42.496
1525 | 42.487
1526 | 42.483
1527 | 42.481
1528 | 42.479
1529 | 42.476
1530 | 42.472
1531 | 42.466
1532 | 42.465
1533 | 42.447
1534 | 42.446
1535 | 42.444
1536 | 42.438
1537 | 42.42
1538 | 42.412
1539 | 42.409
1540 | 42.409
1541 | 42.384
1542 | 42.38
1543 | 42.362
1544 | 42.353
1545 | 42.342
1546 | 42.326
1547 | 42.324
1548 | 42.32
1549 | 42.31
1550 | 42.304
1551 | 42.288
1552 | 42.287
1553 | 42.27
1554 | 42.266
1555 | 42.262
1556 | 42.245
1557 | 42.243
1558 | 42.243
1559 | 42.242
1560 | 42.236
1561 | 42.233
1562 | 42.227
1563 | 42.226
1564 | 42.225
1565 | 42.222
1566 | 42.209
1567 | 42.207
1568 | 42.206
1569 | 42.199
1570 | 42.189
1571 | 42.186
1572 | 42.177
1573 | 42.176
1574 | 42.17
1575 | 42.165
1576 | 42.163
1577 | 42.156
1578 | 42.155
1579 | 42.151
1580 | 42.144
1581 | 42.143
1582 | 42.134
1583 | 42.132
1584 | 42.131
1585 | 42.127
1586 | 42.124
1587 | 42.112
1588 | 42.111
1589 | 42.106
1590 | 42.102
1591 | 42.092
1592 | 42.074
1593 | 42.071
1594 | 42.069
1595 | 42.063
1596 | 42.059
1597 | 42.054
1598 | 42.052
1599 | 42.047
1600 | 42.047
1601 | 42.036
1602 | 42.031
1603 | 42.026
1604 | 42.02
1605 | 42.016
1606 | 42.005
1607 | 42.002
1608 | 41.992
1609 | 41.99
1610 | 41.988
1611 | 41.985
1612 | 41.979
1613 | 41.968
1614 | 41.965
1615 | 41.964
1616 | 41.963
1617 | 41.953
1618 | 41.943
1619 | 41.942
1620 | 41.936
1621 | 41.935
1622 | 41.928
1623 | 41.927
1624 | 41.925
1625 | 41.917
1626 | 41.916
1627 | 41.913
1628 | 41.905
1629 | 41.905
1630 | 41.904
1631 | 41.895
1632 | 41.891
1633 | 41.89
1634 | 41.879
1635 | 41.862
1636 | 41.861
1637 | 41.854
1638 | 41.843
1639 | 41.842
1640 | 41.842
1641 | 41.835
1642 | 41.812
1643 | 41.795
1644 | 41.782
1645 | 41.768
1646 | 41.762
1647 | 41.759
1648 | 41.757
1649 | 41.751
1650 | 41.745
1651 | 41.743
1652 | 41.738
1653 | 41.733
1654 | 41.727
1655 | 41.722
1656 | 41.717
1657 | 41.71
1658 | 41.705
1659 | 41.695
1660 | 41.689
1661 | 41.689
1662 | 41.688
1663 | 41.683
1664 | 41.676
1665 | 41.67
1666 | 41.669
1667 | 41.664
1668 | 41.66
1669 | 41.657
1670 | 41.652
1671 | 41.641
1672 | 41.632
1673 | 41.631
1674 | 41.622
1675 | 41.611
1676 | 41.61
1677 | 41.595
1678 | 41.592
1679 | 41.585
1680 | 41.585
1681 | 41.574
1682 | 41.564
1683 | 41.562
1684 | 41.562
1685 | 41.547
1686 | 41.545
1687 | 41.531
1688 | 41.525
1689 | 41.524
1690 | 41.519
1691 | 41.519
1692 | 41.516
1693 | 41.509
1694 | 41.506
1695 | 41.506
1696 | 41.503
1697 | 41.498
1698 | 41.494
1699 | 41.489
1700 | 41.485
1701 | 41.484
1702 | 41.483
1703 | 41.482
1704 | 41.48
1705 | 41.46
1706 | 41.459
1707 | 41.443
1708 | 41.438
1709 | 41.432
1710 | 41.429
1711 | 41.428
1712 | 41.425
1713 | 41.418
1714 | 41.416
1715 | 41.411
1716 | 41.407
1717 | 41.405
1718 | 41.403
1719 | 41.403
1720 | 41.39
1721 | 41.39
1722 | 41.389
1723 | 41.389
1724 | 41.389
1725 | 41.388
1726 | 41.388
1727 | 41.379
1728 | 41.37
1729 | 41.359
1730 | 41.358
1731 | 41.357
1732 | 41.351
1733 | 41.345
1734 | 41.343
1735 | 41.329
1736 | 41.326
1737 | 41.313
1738 | 41.31
1739 | 41.307
1740 | 41.299
1741 | 41.293
1742 | 41.287
1743 | 41.284
1744 | 41.283
1745 | 41.282
1746 | 41.278
1747 | 41.264
1748 | 41.259
1749 | 41.255
1750 | 41.254
1751 | 41.25
1752 | 41.247
1753 | 41.245
1754 | 41.243
1755 | 41.233
1756 | 41.233
1757 | 41.23
1758 | 41.229
1759 | 41.215
1760 | 41.214
1761 | 41.209
1762 | 41.208
1763 | 41.208
1764 | 41.205
1765 | 41.196
1766 | 41.187
1767 | 41.178
1768 | 41.176
1769 | 41.167
1770 | 41.166
1771 | 41.163
1772 | 41.157
1773 | 41.155
1774 | 41.152
1775 | 41.152
1776 | 41.137
1777 | 41.137
1778 | 41.131
1779 | 41.131
1780 | 41.128
1781 | 41.118
1782 | 41.115
1783 | 41.103
1784 | 41.1
1785 | 41.1
1786 | 41.096
1787 | 41.084
1788 | 41.077
1789 | 41.07
1790 | 41.065
1791 | 41.052
1792 | 41.052
1793 | 41.052
1794 | 41.049
1795 | 41.047
1796 | 41.04
1797 | 41.027
1798 | 41.008
1799 | 41.008
1800 | 41.003
1801 | 41
1802 | 41
1803 | 40.996
1804 | 40.985
1805 | 40.984
1806 | 40.978
1807 | 40.977
1808 | 40.968
1809 | 40.953
1810 | 40.951
1811 | 40.942
1812 | 40.941
1813 | 40.933
1814 | 40.931
1815 | 40.924
1816 | 40.917
1817 | 40.917
1818 | 40.914
1819 | 40.912
1820 | 40.911
1821 | 40.903
1822 | 40.894
1823 | 40.889
1824 | 40.885
1825 | 40.884
1826 | 40.883
1827 | 40.875
1828 | 40.866
1829 | 40.86
1830 | 40.858
1831 | 40.855
1832 | 40.85
1833 | 40.85
1834 | 40.846
1835 | 40.845
1836 | 40.841
1837 | 40.838
1838 | 40.835
1839 | 40.832
1840 | 40.832
1841 | 40.829
1842 | 40.82
1843 | 40.818
1844 | 40.813
1845 | 40.812
1846 | 40.809
1847 | 40.802
1848 | 40.801
1849 | 40.795
1850 | 40.792
1851 | 40.778
1852 | 40.77
1853 | 40.761
1854 | 40.749
1855 | 40.745
1856 | 40.738
1857 | 40.732
1858 | 40.717
1859 | 40.712
1860 | 40.71
1861 | 40.709
1862 | 40.704
1863 | 40.7
1864 | 40.698
1865 | 40.696
1866 | 40.693
1867 | 40.691
1868 | 40.69
1869 | 40.69
1870 | 40.689
1871 | 40.684
1872 | 40.684
1873 | 40.681
1874 | 40.677
1875 | 40.674
1876 | 40.669
1877 | 40.669
1878 | 40.668
1879 | 40.649
1880 | 40.648
1881 | 40.645
1882 | 40.621
1883 | 40.613
1884 | 40.61
1885 | 40.61
1886 | 40.599
1887 | 40.59
1888 | 40.589
1889 | 40.584
1890 | 40.578
1891 | 40.577
1892 | 40.574
1893 | 40.572
1894 | 40.564
1895 | 40.552
1896 | 40.549
1897 | 40.545
1898 | 40.538
1899 | 40.527
1900 | 40.52
1901 | 40.519
1902 | 40.508
1903 | 40.497
1904 | 40.493
1905 | 40.493
1906 | 40.487
1907 | 40.485
1908 | 40.485
1909 | 40.483
1910 | 40.472
1911 | 40.469
1912 | 40.466
1913 | 40.457
1914 | 40.456
1915 | 40.455
1916 | 40.436
1917 | 40.434
1918 | 40.419
1919 | 40.414
1920 | 40.414
1921 | 40.41
1922 | 40.41
1923 | 40.405
1924 | 40.395
1925 | 40.393
1926 | 40.383
1927 | 40.382
1928 | 40.377
1929 | 40.365
1930 | 40.359
1931 | 40.355
1932 | 40.35
1933 | 40.349
1934 | 40.341
1935 | 40.337
1936 | 40.333
1937 | 40.318
1938 | 40.314
1939 | 40.314
1940 | 40.311
1941 | 40.31
1942 | 40.31
1943 | 40.307
1944 | 40.305
1945 | 40.305
1946 | 40.298
1947 | 40.295
1948 | 40.294
1949 | 40.292
1950 | 40.282
1951 | 40.275
1952 | 40.269
1953 | 40.269
1954 | 40.26
1955 | 40.259
1956 | 40.258
1957 | 40.251
1958 | 40.251
1959 | 40.25
1960 | 40.247
1961 | 40.238
1962 | 40.234
1963 | 40.233
1964 | 40.232
1965 | 40.232
1966 | 40.227
1967 | 40.215
1968 | 40.214
1969 | 40.21
1970 | 40.203
1971 | 40.198
1972 | 40.193
1973 | 40.175
1974 | 40.17
1975 | 40.163
1976 | 40.158
1977 | 40.152
1978 | 40.143
1979 | 40.136
1980 | 40.134
1981 | 40.124
1982 | 40.123
1983 | 40.123
1984 | 40.122
1985 | 40.122
1986 | 40.122
1987 | 40.122
1988 | 40.122
1989 | 40.122
1990 | 40.122
1991 | 40.122
1992 | 40.122
1993 | 40.122
1994 | 40.122
1995 | 40.122
1996 | 40.122
1997 | 40.122
1998 | 40.122
1999 | 40.122
2000 | 40.122
2001 | 40.122
2002 | 40.122
2003 | 40.122
2004 | 40.122
2005 | 40.122
2006 | 40.122
2007 | 40.122
2008 | 40.122
2009 | 40.122
2010 | 40.117
2011 | 40.104
2012 | 40.102
2013 | 40.098
2014 | 40.097
2015 | 40.096
2016 | 40.095
2017 | 40.094
2018 | 40.094
2019 | 40.094
2020 | 40.093
2021 | 40.093
2022 | 40.087
2023 | 40.082
2024 | 40.08
2025 | 40.071
2026 | 40.069
2027 | 40.064
2028 | 40.064
2029 | 40.049
2030 | 40.047
2031 | 40.042
2032 | 40.04
2033 | 40.037
2034 | 40.01
2035 | 40.01
2036 | 39.994
2037 | 39.991
2038 | 39.987
2039 | 39.973
2040 | 39.97
2041 | 39.968
2042 | 39.966
2043 | 39.966
2044 | 39.953
2045 | 39.944
2046 | 39.941
2047 | 39.939
2048 | 39.921
2049 | 39.919
2050 | 39.916
2051 | 39.91
2052 | 39.91
2053 | 39.903
2054 | 39.897
2055 | 39.896
2056 | 39.893
2057 | 39.891
2058 | 39.887
2059 | 39.886
2060 | 39.874
2061 | 39.865
2062 | 39.864
2063 | 39.864
2064 | 39.861
2065 | 39.859
2066 | 39.856
2067 | 39.854
2068 | 39.85
2069 | 39.847
2070 | 39.846
2071 | 39.841
2072 | 39.837
2073 | 39.831
2074 | 39.825
2075 | 39.808
2076 | 39.805
2077 | 39.8
2078 | 39.796
2079 | 39.785
2080 | 39.784
2081 | 39.778
2082 | 39.775
2083 | 39.775
2084 | 39.768
2085 | 39.761
2086 | 39.751
2087 | 39.747
2088 | 39.743
2089 | 39.737
2090 | 39.735
2091 | 39.733
2092 | 39.729
2093 | 39.717
2094 | 39.716
2095 | 39.712
2096 | 39.71
2097 | 39.706
2098 | 39.69
2099 | 39.684
2100 | 39.683
2101 | 39.677
2102 | 39.672
2103 | 39.662
2104 | 39.656
2105 | 39.655
2106 | 39.654
2107 | 39.64
2108 | 39.638
2109 | 39.635
2110 | 39.635
2111 | 39.626
2112 | 39.62
2113 | 39.62
2114 | 39.619
2115 | 39.619
2116 | 39.617
2117 | 39.614
2118 | 39.613
2119 | 39.597
2120 | 39.596
2121 | 39.596
2122 | 39.596
2123 | 39.594
2124 | 39.592
2125 | 39.583
2126 | 39.581
2127 | 39.577
2128 | 39.565
2129 | 39.565
2130 | 39.564
2131 | 39.564
2132 | 39.563
2133 | 39.561
2134 | 39.56
2135 | 39.557
2136 | 39.552
2137 | 39.551
2138 | 39.547
2139 | 39.539
2140 | 39.535
2141 | 39.528
2142 | 39.523
2143 | 39.516
2144 | 39.507
2145 | 39.506
2146 | 39.504
2147 | 39.503
2148 | 39.502
2149 | 39.5
2150 | 39.497
2151 | 39.497
2152 | 39.49
2153 | 39.487
2154 | 39.481
2155 | 39.476
2156 | 39.473
2157 | 39.461
2158 | 39.447
2159 | 39.442
2160 | 39.44
2161 | 39.438
2162 | 39.438
2163 | 39.438
2164 | 39.437
2165 | 39.432
2166 | 39.419
2167 | 39.416
2168 | 39.401
2169 | 39.387
2170 | 39.385
2171 | 39.379
2172 | 39.374
2173 | 39.372
2174 | 39.362
2175 | 39.361
2176 | 39.355
2177 | 39.354
2178 | 39.348
2179 | 39.347
2180 | 39.347
2181 | 39.343
2182 | 39.339
2183 | 39.33
2184 | 39.324
2185 | 39.323
2186 | 39.321
2187 | 39.32
2188 | 39.313
2189 | 39.311
2190 | 39.311
2191 | 39.308
2192 | 39.307
2193 | 39.304
2194 | 39.294
2195 | 39.29
2196 | 39.288
2197 | 39.287
2198 | 39.285
2199 | 39.284
2200 | 39.269
2201 | 39.265
2202 | 39.264
2203 | 39.262
2204 | 39.256
2205 | 39.25
2206 | 39.241
2207 | 39.229
2208 | 39.226
2209 | 39.216
2210 | 39.215
2211 | 39.211
2212 | 39.207
2213 | 39.201
2214 | 39.199
2215 | 39.195
2216 | 39.184
2217 | 39.18
2218 | 39.176
2219 | 39.172
2220 | 39.17
2221 | 39.162
2222 | 39.16
2223 | 39.159
2224 | 39.156
2225 | 39.151
2226 | 39.147
2227 | 39.146
2228 | 39.145
2229 | 39.143
2230 | 39.13
2231 | 39.13
2232 | 39.128
2233 | 39.123
2234 | 39.121
2235 | 39.119
2236 | 39.117
2237 | 39.113
2238 | 39.112
2239 | 39.1
2240 | 39.097
2241 | 39.094
2242 | 39.093
2243 | 39.092
2244 | 39.091
2245 | 39.088
2246 | 39.088
2247 | 39.085
2248 | 39.084
2249 | 39.08
2250 | 39.069
2251 | 39.067
2252 | 39.059
2253 | 39.058
2254 | 39.055
2255 | 39.054
2256 | 39.05
2257 | 39.044
2258 | 39.04
2259 | 39.039
2260 | 39.025
2261 | 39.022
2262 | 39.019
2263 | 39.015
2264 | 39.011
2265 | 39.011
2266 | 39.01
2267 | 39.008
2268 | 39.007
2269 | 39.006
2270 | 39.004
2271 | 39.003
2272 | 39.002
2273 | 39.002
2274 | 39.001
2275 | 38.999
2276 | 38.993
2277 | 38.992
2278 | 38.991
2279 | 38.985
2280 | 38.98
2281 | 38.97
2282 | 38.955
2283 | 38.95
2284 | 38.939
2285 | 38.934
2286 | 38.931
2287 | 38.93
2288 | 38.925
2289 | 38.923
2290 | 38.921
2291 | 38.915
2292 | 38.913
2293 | 38.905
2294 | 38.885
2295 | 38.884
2296 | 38.883
2297 | 38.879
2298 | 38.869
2299 | 38.869
2300 | 38.855
2301 | 38.851
2302 | 38.851
2303 | 38.847
2304 | 38.847
2305 | 38.842
2306 | 38.84
2307 | 38.839
2308 | 38.833
2309 | 38.827
2310 | 38.825
2311 | 38.824
2312 | 38.819
2313 | 38.818
2314 | 38.818
2315 | 38.811
2316 | 38.809
2317 | 38.809
2318 | 38.798
2319 | 38.797
2320 | 38.794
2321 | 38.785
2322 | 38.785
2323 | 38.779
2324 | 38.765
2325 | 38.759
2326 | 38.755
2327 | 38.747
2328 | 38.745
2329 | 38.741
2330 | 38.731
2331 | 38.725
2332 | 38.721
2333 | 38.718
2334 | 38.717
2335 | 38.717
2336 | 38.711
2337 | 38.709
2338 | 38.708
2339 | 38.708
2340 | 38.701
2341 | 38.698
2342 | 38.689
2343 | 38.683
2344 | 38.682
2345 | 38.677
2346 | 38.677
2347 | 38.674
2348 | 38.672
2349 | 38.67
2350 | 38.669
2351 | 38.657
2352 | 38.654
2353 | 38.645
2354 | 38.638
2355 | 38.636
2356 | 38.636
2357 | 38.635
2358 | 38.628
2359 | 38.623
2360 | 38.62
2361 | 38.619
2362 | 38.617
2363 | 38.612
2364 | 38.61
2365 | 38.61
2366 | 38.61
2367 | 38.608
2368 | 38.606
2369 | 38.599
2370 | 38.597
2371 | 38.597
2372 | 38.594
2373 | 38.59
2374 | 38.586
2375 | 38.586
2376 | 38.585
2377 | 38.582
2378 | 38.581
2379 | 38.576
2380 | 38.57
2381 | 38.567
2382 | 38.563
2383 | 38.562
2384 | 38.549
2385 | 38.548
2386 | 38.535
2387 | 38.534
2388 | 38.533
2389 | 38.533
2390 | 38.532
2391 | 38.532
2392 | 38.531
2393 | 38.526
2394 | 38.51
2395 | 38.506
2396 | 38.5
2397 | 38.5
2398 | 38.498
2399 | 38.49
2400 | 38.489
2401 | 38.489
2402 | 38.484
2403 | 38.477
2404 | 38.475
2405 | 38.473
2406 | 38.465
2407 | 38.461
2408 | 38.448
2409 | 38.446
2410 | 38.444
2411 | 38.441
2412 | 38.436
2413 | 38.436
2414 | 38.435
2415 | 38.428
2416 | 38.427
2417 | 38.424
2418 | 38.417
2419 | 38.412
2420 | 38.407
2421 | 38.401
2422 | 38.397
2423 | 38.391
2424 | 38.387
2425 | 38.382
2426 | 38.375
2427 | 38.367
2428 | 38.359
2429 | 38.357
2430 | 38.356
2431 | 38.355
2432 | 38.354
2433 | 38.345
2434 | 38.34
2435 | 38.336
2436 | 38.332
2437 | 38.331
2438 | 38.33
2439 | 38.326
2440 | 38.314
2441 | 38.312
2442 | 38.308
2443 | 38.307
2444 | 38.306
2445 | 38.305
2446 | 38.303
2447 | 38.295
2448 | 38.293
2449 | 38.292
2450 | 38.292
2451 | 38.29
2452 | 38.289
2453 | 38.287
2454 | 38.276
2455 | 38.274
2456 | 38.271
2457 | 38.266
2458 | 38.266
2459 | 38.261
2460 | 38.259
2461 | 38.258
2462 | 38.252
2463 | 38.25
2464 | 38.241
2465 | 38.235
2466 | 38.234
2467 | 38.228
2468 | 38.228
2469 | 38.214
2470 | 38.212
2471 | 38.211
2472 | 38.208
2473 | 38.207
2474 | 38.206
2475 | 38.205
2476 | 38.198
2477 | 38.195
2478 | 38.193
2479 | 38.179
2480 | 38.175
2481 | 38.172
2482 | 38.172
2483 | 38.166
2484 | 38.166
2485 | 38.166
2486 | 38.164
2487 | 38.161
2488 | 38.161
2489 | 38.159
2490 | 38.159
2491 | 38.153
2492 | 38.153
2493 | 38.136
2494 | 38.131
2495 | 38.116
2496 | 38.113
2497 | 38.111
2498 | 38.107
2499 | 38.105
2500 | 38.104
2501 | 38.099
2502 | 38.099
2503 | 38.096
2504 | 38.096
2505 | 38.088
2506 | 38.081
2507 | 38.077
2508 | 38.074
2509 | 38.072
2510 | 38.069
2511 | 38.066
2512 | 38.065
2513 | 38.064
2514 | 38.059
2515 | 38.053
2516 | 38.053
2517 | 38.047
2518 | 38.047
2519 | 38.047
2520 | 38.041
2521 | 38.04
2522 | 38.039
2523 | 38.038
2524 | 38.031
2525 | 38.026
2526 | 38.021
2527 | 38.019
2528 | 38.017
2529 | 38.017
2530 | 38.014
2531 | 38.007
2532 | 38.007
2533 | 38.007
2534 | 38.005
2535 | 38.003
2536 | 38
2537 | 37.996
2538 | 37.994
2539 | 37.994
2540 | 37.989
2541 | 37.989
2542 | 37.988
2543 | 37.981
2544 | 37.978
2545 | 37.971
2546 | 37.966
2547 | 37.965
2548 | 37.965
2549 | 37.962
2550 | 37.962
2551 | 37.956
2552 | 37.944
2553 | 37.943
2554 | 37.939
2555 | 37.932
2556 | 37.931
2557 | 37.927
2558 | 37.926
2559 | 37.919
2560 | 37.913
2561 | 37.912
2562 | 37.896
2563 | 37.896
2564 | 37.895
2565 | 37.895
2566 | 37.893
2567 | 37.892
2568 | 37.888
2569 | 37.888
2570 | 37.888
2571 | 37.886
2572 | 37.878
2573 | 37.875
2574 | 37.871
2575 | 37.871
2576 | 37.871
2577 | 37.869
2578 | 37.867
2579 | 37.863
2580 | 37.861
2581 | 37.859
2582 | 37.855
2583 | 37.855
2584 | 37.851
2585 | 37.85
2586 | 37.846
2587 | 37.845
2588 | 37.841
2589 | 37.84
2590 | 37.832
2591 | 37.824
2592 | 37.824
2593 | 37.822
2594 | 37.815
2595 | 37.815
2596 | 37.81
2597 | 37.794
2598 | 37.786
2599 | 37.781
2600 | 37.774
2601 | 37.774
2602 | 37.772
2603 | 37.763
2604 | 37.761
2605 | 37.758
2606 | 37.757
2607 | 37.755
2608 | 37.751
2609 | 37.747
2610 | 37.745
2611 | 37.744
2612 | 37.738
2613 | 37.729
2614 | 37.728
2615 | 37.716
2616 | 37.711
2617 | 37.704
2618 | 37.703
2619 | 37.7
2620 | 37.695
2621 | 37.694
2622 | 37.681
2623 | 37.675
2624 | 37.673
2625 | 37.665
2626 | 37.662
2627 | 37.661
2628 | 37.661
2629 | 37.66
2630 | 37.659
2631 | 37.656
2632 | 37.646
2633 | 37.643
2634 | 37.637
2635 | 37.636
2636 | 37.635
2637 | 37.634
2638 | 37.633
2639 | 37.631
2640 | 37.625
2641 | 37.623
2642 | 37.619
2643 | 37.616
2644 | 37.616
2645 | 37.613
2646 | 37.611
2647 | 37.611
2648 | 37.609
2649 | 37.607
2650 | 37.607
2651 | 37.605
2652 | 37.604
2653 | 37.595
2654 | 37.594
2655 | 37.59
2656 | 37.589
2657 | 37.589
2658 | 37.585
2659 | 37.58
2660 | 37.58
2661 | 37.578
2662 | 37.573
2663 | 37.572
2664 | 37.569
2665 | 37.565
2666 | 37.565
2667 | 37.564
2668 | 37.562
2669 | 37.554
2670 | 37.549
2671 | 37.543
2672 | 37.542
2673 | 37.541
2674 | 37.54
2675 | 37.537
2676 | 37.536
2677 | 37.535
2678 | 37.532
2679 | 37.528
2680 | 37.522
2681 | 37.522
2682 | 37.521
2683 | 37.514
2684 | 37.508
2685 | 37.505
2686 | 37.504
2687 | 37.502
2688 | 37.501
2689 | 37.5
2690 | 37.498
2691 | 37.49
2692 | 37.488
2693 | 37.487
2694 | 37.486
2695 | 37.483
2696 | 37.483
2697 | 37.482
2698 | 37.471
2699 | 37.464
2700 | 37.463
2701 | 37.463
2702 | 37.452
2703 | 37.452
2704 | 37.445
2705 | 37.444
2706 | 37.443
2707 | 37.443
2708 | 37.434
2709 | 37.432
2710 | 37.432
2711 | 37.427
2712 | 37.416
2713 | 37.416
2714 | 37.413
2715 | 37.413
2716 | 37.412
2717 | 37.402
2718 | 37.397
2719 | 37.383
2720 | 37.383
2721 | 37.382
2722 | 37.376
2723 | 37.369
2724 | 37.367
2725 | 37.367
2726 | 37.362
2727 | 37.357
2728 | 37.353
2729 | 37.352
2730 | 37.351
2731 | 37.345
2732 | 37.345
2733 | 37.342
2734 | 37.341
2735 | 37.332
2736 | 37.331
2737 | 37.327
2738 | 37.325
2739 | 37.322
2740 | 37.319
2741 | 37.319
2742 | 37.318
2743 | 37.315
2744 | 37.308
2745 | 37.304
2746 | 37.297
2747 | 37.293
2748 | 37.292
2749 | 37.288
2750 | 37.286
2751 | 37.285
2752 | 37.278
2753 | 37.277
2754 | 37.272
2755 | 37.269
2756 | 37.268
2757 | 37.265
2758 | 37.265
2759 | 37.264
2760 | 37.263
2761 | 37.262
2762 | 37.255
2763 | 37.254
2764 | 37.25
2765 | 37.241
2766 | 37.24
2767 | 37.24
2768 | 37.239
2769 | 37.236
2770 | 37.232
2771 | 37.229
2772 | 37.228
2773 | 37.228
2774 | 37.228
2775 | 37.228
2776 | 37.222
2777 | 37.221
2778 | 37.217
2779 | 37.216
2780 | 37.215
2781 | 37.214
2782 | 37.21
2783 | 37.206
2784 | 37.206
2785 | 37.205
2786 | 37.203
2787 | 37.199
2788 | 37.198
2789 | 37.196
2790 | 37.189
2791 | 37.188
2792 | 37.185
2793 | 37.183
2794 | 37.182
2795 | 37.182
2796 | 37.175
2797 | 37.173
2798 | 37.168
2799 | 37.158
2800 | 37.155
2801 | 37.155
2802 | 37.153
2803 | 37.149
2804 | 37.149
2805 | 37.148
2806 | 37.141
2807 | 37.137
2808 | 37.117
2809 | 37.116
2810 | 37.112
2811 | 37.107
2812 | 37.106
2813 | 37.103
2814 | 37.103
2815 | 37.102
2816 | 37.1
2817 | 37.098
2818 | 37.095
2819 | 37.093
2820 | 37.079
2821 | 37.075
2822 | 37.074
2823 | 37.072
2824 | 37.071
2825 | 37.068
2826 | 37.066
2827 | 37.064
2828 | 37.063
2829 | 37.049
2830 | 37.047
2831 | 37.044
2832 | 37.044
2833 | 37.043
2834 | 37.041
2835 | 37.038
2836 | 37.032
2837 | 37.031
2838 | 37.029
2839 | 37.018
2840 | 37.018
2841 | 37.011
2842 | 37.011
2843 | 37.011
2844 | 37.008
2845 | 37.007
2846 | 37.006
2847 | 37.006
2848 | 37.004
2849 | 37.003
2850 | 37.001
2851 | 36.999
2852 | 36.999
2853 | 36.999
2854 | 36.998
2855 | 36.998
2856 | 36.996
2857 | 36.995
2858 | 36.991
2859 | 36.987
2860 | 36.986
2861 | 36.984
2862 | 36.983
2863 | 36.973
2864 | 36.964
2865 | 36.963
2866 | 36.961
2867 | 36.96
2868 | 36.96
2869 | 36.959
2870 | 36.956
2871 | 36.953
2872 | 36.953
2873 | 36.952
2874 | 36.951
2875 | 36.95
2876 | 36.948
2877 | 36.943
2878 | 36.939
2879 | 36.936
2880 | 36.934
2881 | 36.928
2882 | 36.925
2883 | 36.923
2884 | 36.92
2885 | 36.916
2886 | 36.913
2887 | 36.91
2888 | 36.908
2889 | 36.908
2890 | 36.907
2891 | 36.904
2892 | 36.903
2893 | 36.9
2894 | 36.897
2895 | 36.895
2896 | 36.894
2897 | 36.893
2898 | 36.89
2899 | 36.883
2900 | 36.882
2901 | 36.877
2902 | 36.874
2903 | 36.869
2904 | 36.868
2905 | 36.867
2906 | 36.862
2907 | 36.859
2908 | 36.857
2909 | 36.855
2910 | 36.853
2911 | 36.85
2912 | 36.843
2913 | 36.843
2914 | 36.839
2915 | 36.838
2916 | 36.829
2917 | 36.827
2918 | 36.824
2919 | 36.821
2920 | 36.817
2921 | 36.815
2922 | 36.812
2923 | 36.811
2924 | 36.808
2925 | 36.808
2926 | 36.802
2927 | 36.792
2928 | 36.789
2929 | 36.789
2930 | 36.788
2931 | 36.782
2932 | 36.779
2933 | 36.775
2934 | 36.766
2935 | 36.763
2936 | 36.759
2937 | 36.759
2938 | 36.756
2939 | 36.752
2940 | 36.751
2941 | 36.746
2942 | 36.744
2943 | 36.739
2944 | 36.732
2945 | 36.732
2946 | 36.73
2947 | 36.727
2948 | 36.725
2949 | 36.721
2950 | 36.718
2951 | 36.717
2952 | 36.714
2953 | 36.71
2954 | 36.707
2955 | 36.703
2956 | 36.701
2957 | 36.693
2958 | 36.692
2959 | 36.689
2960 | 36.686
2961 | 36.686
2962 | 36.682
2963 | 36.679
2964 | 36.679
2965 | 36.675
2966 | 36.674
2967 | 36.671
2968 | 36.671
2969 | 36.671
2970 | 36.669
2971 | 36.667
2972 | 36.664
2973 | 36.662
2974 | 36.662
2975 | 36.66
2976 | 36.66
2977 | 36.657
2978 | 36.657
2979 | 36.656
2980 | 36.649
2981 | 36.648
2982 | 36.648
2983 | 36.64
2984 | 36.636
2985 | 36.635
2986 | 36.622
2987 | 36.619
2988 | 36.616
2989 | 36.616
2990 | 36.616
2991 | 36.614
2992 | 36.605
2993 | 36.6
2994 | 36.599
2995 | 36.586
2996 | 36.586
2997 | 36.583
2998 | 36.577
2999 | 36.574
3000 | 36.574
3001 | 36.573
3002 | 36.572
3003 | 36.571
3004 | 36.567
3005 | 36.562
3006 | 36.56
3007 | 36.559
3008 | 36.554
3009 | 36.544
3010 | 36.54
3011 | 36.54
3012 | 36.527
3013 | 36.527
3014 | 36.524
3015 | 36.519
3016 | 36.515
3017 | 36.514
3018 | 36.509
3019 | 36.508
3020 | 36.507
3021 | 36.506
3022 | 36.502
3023 | 36.501
3024 | 36.501
3025 | 36.494
3026 | 36.493
3027 | 36.489
3028 | 36.487
3029 | 36.485
3030 | 36.482
3031 | 36.48
3032 | 36.466
3033 | 36.459
3034 | 36.453
3035 | 36.451
3036 | 36.449
3037 | 36.448
3038 | 36.448
3039 | 36.447
3040 | 36.446
3041 | 36.443
3042 | 36.44
3043 | 36.433
3044 | 36.43
3045 | 36.428
3046 | 36.425
3047 | 36.423
3048 | 36.419
3049 | 36.418
3050 | 36.418
3051 | 36.416
3052 | 36.409
3053 | 36.408
3054 | 36.407
3055 | 36.404
3056 | 36.402
3057 | 36.387
3058 | 36.384
3059 | 36.382
3060 | 36.374
3061 | 36.372
3062 | 36.371
3063 | 36.369
3064 | 36.367
3065 | 36.361
3066 | 36.356
3067 | 36.353
3068 | 36.352
3069 | 36.35
3070 | 36.348
3071 | 36.345
3072 | 36.34
3073 | 36.334
3074 | 36.334
3075 | 36.33
3076 | 36.325
3077 | 36.316
3078 | 36.314
3079 | 36.307
3080 | 36.306
3081 | 36.304
3082 | 36.302
3083 | 36.301
3084 | 36.299
3085 | 36.289
3086 | 36.289
3087 | 36.285
3088 | 36.285
3089 | 36.278
3090 | 36.275
3091 | 36.271
3092 | 36.269
3093 | 36.269
3094 | 36.269
3095 | 36.267
3096 | 36.265
3097 | 36.263
3098 | 36.259
3099 | 36.259
3100 | 36.254
3101 | 36.248
3102 | 36.238
3103 | 36.236
3104 | 36.235
3105 | 36.228
3106 | 36.224
3107 | 36.223
3108 | 36.223
3109 | 36.22
3110 | 36.219
3111 | 36.216
3112 | 36.214
3113 | 36.213
3114 | 36.211
3115 | 36.211
3116 | 36.207
3117 | 36.206
3118 | 36.205
3119 | 36.204
3120 | 36.198
3121 | 36.195
3122 | 36.192
3123 | 36.192
3124 | 36.19
3125 | 36.185
3126 | 36.185
3127 | 36.184
3128 | 36.182
3129 | 36.18
3130 | 36.177
3131 | 36.171
3132 | 36.171
3133 | 36.17
3134 | 36.17
3135 | 36.16
3136 | 36.158
3137 | 36.154
3138 | 36.151
3139 | 36.147
3140 | 36.141
3141 | 36.14
3142 | 36.121
3143 | 36.116
3144 | 36.115
3145 | 36.107
3146 | 36.106
3147 | 36.103
3148 | 36.103
3149 | 36.098
3150 | 36.096
3151 | 36.087
3152 | 36.087
3153 | 36.086
3154 | 36.082
3155 | 36.081
3156 | 36.079
3157 | 36.073
3158 | 36.073
3159 | 36.067
3160 | 36.066
3161 | 36.057
3162 | 36.054
3163 | 36.052
3164 | 36.051
3165 | 36.049
3166 | 36.048
3167 | 36.046
3168 | 36.041
3169 | 36.041
3170 | 36.041
3171 | 36.034
3172 | 36.032
3173 | 36.032
3174 | 36.029
3175 | 36.028
3176 | 36.025
3177 | 36.022
3178 | 36.021
3179 | 36.019
3180 | 36.019
3181 | 36.017
3182 | 36.017
3183 | 36.016
3184 | 36.015
3185 | 36.013
3186 | 36.008
3187 | 36.008
3188 | 36.002
3189 | 35.999
3190 | 35.998
3191 | 35.998
3192 | 35.988
3193 | 35.983
3194 | 35.982
3195 | 35.979
3196 | 35.978
3197 | 35.973
3198 | 35.972
3199 | 35.97
3200 | 35.964
3201 | 35.961
3202 | 35.957
3203 | 35.956
3204 | 35.951
3205 | 35.951
3206 | 35.949
3207 | 35.949
3208 | 35.945
3209 | 35.945
3210 | 35.944
3211 | 35.944
3212 | 35.942
3213 | 35.939
3214 | 35.936
3215 | 35.935
3216 | 35.932
3217 | 35.931
3218 | 35.93
3219 | 35.929
3220 | 35.915
3221 | 35.915
3222 | 35.915
3223 | 35.912
3224 | 35.912
3225 | 35.912
3226 | 35.901
3227 | 35.897
3228 | 35.896
3229 | 35.895
3230 | 35.895
3231 | 35.894
3232 | 35.89
3233 | 35.889
3234 | 35.887
3235 | 35.882
3236 | 35.868
3237 | 35.867
3238 | 35.865
3239 | 35.865
3240 | 35.865
3241 | 35.863
3242 | 35.859
3243 | 35.853
3244 | 35.848
3245 | 35.846
3246 | 35.844
3247 | 35.832
3248 | 35.828
3249 | 35.828
3250 | 35.827
3251 | 35.825
3252 | 35.822
3253 | 35.821
3254 | 35.82
3255 | 35.819
3256 | 35.817
3257 | 35.811
3258 | 35.803
3259 | 35.797
3260 | 35.781
3261 | 35.781
3262 | 35.779
3263 | 35.778
3264 | 35.778
3265 | 35.777
3266 | 35.775
3267 | 35.775
3268 | 35.775
3269 | 35.774
3270 | 35.77
3271 | 35.77
3272 | 35.767
3273 | 35.763
3274 | 35.762
3275 | 35.762
3276 | 35.761
3277 | 35.76
3278 | 35.756
3279 | 35.752
3280 | 35.75
3281 | 35.742
3282 | 35.741
3283 | 35.741
3284 | 35.737
3285 | 35.734
3286 | 35.731
3287 | 35.728
3288 | 35.724
3289 | 35.722
3290 | 35.722
3291 | 35.721
3292 | 35.716
3293 | 35.714
3294 | 35.713
3295 | 35.713
3296 | 35.712
3297 | 35.711
3298 | 35.71
3299 | 35.71
3300 | 35.709
3301 | 35.706
3302 | 35.706
3303 | 35.699
3304 | 35.694
3305 | 35.69
3306 | 35.686
3307 | 35.672
3308 | 35.672
3309 | 35.671
3310 | 35.669
3311 | 35.647
3312 | 35.641
3313 | 35.637
3314 | 35.636
3315 | 35.635
3316 | 35.634
3317 | 35.631
3318 | 35.629
3319 | 35.628
3320 | 35.627
3321 | 35.624
3322 | 35.619
3323 | 35.618
3324 | 35.615
3325 | 35.612
3326 | 35.609
3327 | 35.604
3328 | 35.603
3329 | 35.597
3330 | 35.595
3331 | 35.591
3332 | 35.59
3333 | 35.588
3334 | 35.586
3335 | 35.58
3336 | 35.577
3337 | 35.576
3338 | 35.569
3339 | 35.567
3340 | 35.567
3341 | 35.565
3342 | 35.561
3343 | 35.56
3344 | 35.559
3345 | 35.557
3346 | 35.556
3347 | 35.555
3348 | 35.554
3349 | 35.541
3350 | 35.532
3351 | 35.522
3352 | 35.519
3353 | 35.518
3354 | 35.517
3355 | 35.516
3356 | 35.516
3357 | 35.508
3358 | 35.508
3359 | 35.5
3360 | 35.499
3361 | 35.493
3362 | 35.492
3363 | 35.491
3364 | 35.491
3365 | 35.488
3366 | 35.488
3367 | 35.485
3368 | 35.484
3369 | 35.483
3370 | 35.479
3371 | 35.472
3372 | 35.47
3373 | 35.469
3374 | 35.469
3375 | 35.466
3376 | 35.46
3377 | 35.456
3378 | 35.455
3379 | 35.451
3380 | 35.448
3381 | 35.448
3382 | 35.448
3383 | 35.448
3384 | 35.447
3385 | 35.438
3386 | 35.437
3387 | 35.434
3388 | 35.433
3389 | 35.432
3390 | 35.43
3391 | 35.422
3392 | 35.421
3393 | 35.421
3394 | 35.42
3395 | 35.416
3396 | 35.416
3397 | 35.416
3398 | 35.412
3399 | 35.411
3400 | 35.409
3401 | 35.409
3402 | 35.406
3403 | 35.405
3404 | 35.401
3405 | 35.4
3406 | 35.4
3407 | 35.399
3408 | 35.399
3409 | 35.398
3410 | 35.395
3411 | 35.394
3412 | 35.394
3413 | 35.393
3414 | 35.393
3415 | 35.39
3416 | 35.385
3417 | 35.383
3418 | 35.383
3419 | 35.376
3420 | 35.374
3421 | 35.372
3422 | 35.372
3423 | 35.369
3424 | 35.369
3425 | 35.368
3426 | 35.367
3427 | 35.365
3428 | 35.36
3429 | 35.36
3430 | 35.357
3431 | 35.353
3432 | 35.35
3433 | 35.349
3434 | 35.346
3435 | 35.346
3436 | 35.345
3437 | 35.344
3438 | 35.337
3439 | 35.328
3440 | 35.326
3441 | 35.324
3442 | 35.324
3443 | 35.324
3444 | 35.322
3445 | 35.32
3446 | 35.319
3447 | 35.319
3448 | 35.318
3449 | 35.317
3450 | 35.316
3451 | 35.316
3452 | 35.313
3453 | 35.313
3454 | 35.306
3455 | 35.304
3456 | 35.303
3457 | 35.303
3458 | 35.301
3459 | 35.299
3460 | 35.299
3461 | 35.298
3462 | 35.295
3463 | 35.295
3464 | 35.294
3465 | 35.29
3466 | 35.289
3467 | 35.286
3468 | 35.282
3469 | 35.28
3470 | 35.28
3471 | 35.271
3472 | 35.27
3473 | 35.268
3474 | 35.267
3475 | 35.266
3476 | 35.263
3477 | 35.262
3478 | 35.261
3479 | 35.259
3480 | 35.259
3481 | 35.254
3482 | 35.25
3483 | 35.248
3484 | 35.248
3485 | 35.244
3486 | 35.243
3487 | 35.242
3488 | 35.24
3489 | 35.235
3490 | 35.234
3491 | 35.233
3492 | 35.232
3493 | 35.232
3494 | 35.225
3495 | 35.224
3496 | 35.218
3497 | 35.217
3498 | 35.216
3499 | 35.216
3500 | 35.214
3501 | 35.213
3502 | 35.213
3503 | 35.209
3504 | 35.208
3505 | 35.206
3506 | 35.202
3507 | 35.2
3508 | 35.195
3509 | 35.192
3510 | 35.183
3511 | 35.183
3512 | 35.179
3513 | 35.177
3514 | 35.171
3515 | 35.168
3516 | 35.167
3517 | 35.165
3518 | 35.165
3519 | 35.164
3520 | 35.161
3521 | 35.158
3522 | 35.155
3523 | 35.153
3524 | 35.151
3525 | 35.145
3526 | 35.144
3527 | 35.141
3528 | 35.14
3529 | 35.138
3530 | 35.13
3531 | 35.129
3532 | 35.128
3533 | 35.127
3534 | 35.121
3535 | 35.12
3536 | 35.119
3537 | 35.118
3538 | 35.114
3539 | 35.108
3540 | 35.108
3541 | 35.106
3542 | 35.105
3543 | 35.102
3544 | 35.099
3545 | 35.099
3546 | 35.099
3547 | 35.098
3548 | 35.094
3549 | 35.092
3550 | 35.09
3551 | 35.089
3552 | 35.088
3553 | 35.087
3554 | 35.084
3555 | 35.084
3556 | 35.083
3557 | 35.079
3558 | 35.078
3559 | 35.078
3560 | 35.075
3561 | 35.074
3562 | 35.072
3563 | 35.071
3564 | 35.071
3565 | 35.068
3566 | 35.067
3567 | 35.065
3568 | 35.065
3569 | 35.063
3570 | 35.062
3571 | 35.061
3572 | 35.058
3573 | 35.058
3574 | 35.057
3575 | 35.055
3576 | 35.051
3577 | 35.046
3578 | 35.044
3579 | 35.04
3580 | 35.038
3581 | 35.038
3582 | 35.036
3583 | 35.034
3584 | 35.034
3585 | 35.032
3586 | 35.03
3587 | 35.03
3588 | 35.018
3589 | 35.013
3590 | 35.012
3591 | 35.011
3592 | 35.011
3593 | 35.011
3594 | 35.007
3595 | 35.004
3596 | 34.995
3597 | 34.993
3598 | 34.99
3599 | 34.984
3600 | 34.984
3601 | 34.982
3602 | 34.981
3603 | 34.977
3604 | 34.976
3605 | 34.972
3606 | 34.972
3607 | 34.972
3608 | 34.971
3609 | 34.967
3610 | 34.958
3611 | 34.956
3612 | 34.955
3613 | 34.95
3614 | 34.947
3615 | 34.947
3616 | 34.945
3617 | 34.945
3618 | 34.944
3619 | 34.943
3620 | 34.943
3621 | 34.941
3622 | 34.937
3623 | 34.916
3624 | 34.914
3625 | 34.911
3626 | 34.91
3627 | 34.907
3628 | 34.905
3629 | 34.903
3630 | 34.903
3631 | 34.901
3632 | 34.901
3633 | 34.9
3634 | 34.899
3635 | 34.896
3636 | 34.894
3637 | 34.894
3638 | 34.892
3639 | 34.89
3640 | 34.889
3641 | 34.888
3642 | 34.885
3643 | 34.884
3644 | 34.879
3645 | 34.878
3646 | 34.878
3647 | 34.873
3648 | 34.871
3649 | 34.866
3650 | 34.861
3651 | 34.861
3652 | 34.859
3653 | 34.855
3654 | 34.851
3655 | 34.848
3656 | 34.846
3657 | 34.844
3658 | 34.842
3659 | 34.84
3660 | 34.836
3661 | 34.832
3662 | 34.83
3663 | 34.828
3664 | 34.828
3665 | 34.828
3666 | 34.826
3667 | 34.82
3668 | 34.817
3669 | 34.815
3670 | 34.812
3671 | 34.812
3672 | 34.808
3673 | 34.808
3674 | 34.808
3675 | 34.804
3676 | 34.803
3677 | 34.801
3678 | 34.801
3679 | 34.792
3680 | 34.792
3681 | 34.789
3682 | 34.788
3683 | 34.786
3684 | 34.783
3685 | 34.781
3686 | 34.78
3687 | 34.774
3688 | 34.773
3689 | 34.773
3690 | 34.772
3691 | 34.771
3692 | 34.771
3693 | 34.767
3694 | 34.765
3695 | 34.763
3696 | 34.763
3697 | 34.763
3698 | 34.757
3699 | 34.752
3700 | 34.751
3701 | 34.751
3702 | 34.748
3703 | 34.747
3704 | 34.746
3705 | 34.745
3706 | 34.744
3707 | 34.743
3708 | 34.741
3709 | 34.74
3710 | 34.736
3711 | 34.733
3712 | 34.73
3713 | 34.726
3714 | 34.724
3715 | 34.72
3716 | 34.72
3717 | 34.717
3718 | 34.715
3719 | 34.714
3720 | 34.713
3721 | 34.709
3722 | 34.708
3723 | 34.702
3724 | 34.698
3725 | 34.697
3726 | 34.697
3727 | 34.694
3728 | 34.694
3729 | 34.686
3730 | 34.686
3731 | 34.685
3732 | 34.685
3733 | 34.679
3734 | 34.679
3735 | 34.679
3736 | 34.675
3737 | 34.674
3738 | 34.671
3739 | 34.668
3740 | 34.667
3741 | 34.667
3742 | 34.664
3743 | 34.663
3744 | 34.662
3745 | 34.66
3746 | 34.659
3747 | 34.656
3748 | 34.65
3749 | 34.648
3750 | 34.641
3751 | 34.638
3752 | 34.636
3753 | 34.635
3754 | 34.633
3755 | 34.632
3756 | 34.63
3757 | 34.629
3758 | 34.628
3759 | 34.627
3760 | 34.626
3761 | 34.626
3762 | 34.625
3763 | 34.624
3764 | 34.623
3765 | 34.617
3766 | 34.612
3767 | 34.612
3768 | 34.608
3769 | 34.607
3770 | 34.607
3771 | 34.604
3772 | 34.598
3773 | 34.595
3774 | 34.592
3775 | 34.591
3776 | 34.59
3777 | 34.59
3778 | 34.589
3779 | 34.588
3780 | 34.586
3781 | 34.577
3782 | 34.576
3783 | 34.573
3784 | 34.569
3785 | 34.562
3786 | 34.561
3787 | 34.561
3788 | 34.561
3789 | 34.558
3790 | 34.556
3791 | 34.554
3792 | 34.551
3793 | 34.55
3794 | 34.548
3795 | 34.545
3796 | 34.542
3797 | 34.535
3798 | 34.535
3799 | 34.534
3800 | 34.528
3801 | 34.528
3802 | 34.528
3803 | 34.524
3804 | 34.523
3805 | 34.522
3806 | 34.521
3807 | 34.519
3808 | 34.514
3809 | 34.512
3810 | 34.509
3811 | 34.509
3812 | 34.508
3813 | 34.506
3814 | 34.506
3815 | 34.505
3816 | 34.505
3817 | 34.505
3818 | 34.502
3819 | 34.501
3820 | 34.498
3821 | 34.498
3822 | 34.497
3823 | 34.493
3824 | 34.487
3825 | 34.486
3826 | 34.484
3827 | 34.484
3828 | 34.483
3829 | 34.48
3830 | 34.478
3831 | 34.477
3832 | 34.474
3833 | 34.472
3834 | 34.469
3835 | 34.468
3836 | 34.465
3837 | 34.46
3838 | 34.46
3839 | 34.456
3840 | 34.453
3841 | 34.447
3842 | 34.442
3843 | 34.435
3844 | 34.432
3845 | 34.428
3846 | 34.427
3847 | 34.426
3848 | 34.425
3849 | 34.425
3850 | 34.424
3851 | 34.419
3852 | 34.419
3853 | 34.419
3854 | 34.418
3855 | 34.414
3856 | 34.41
3857 | 34.406
3858 | 34.406
3859 | 34.405
3860 | 34.403
3861 | 34.402
3862 | 34.401
3863 | 34.4
3864 | 34.4
3865 | 34.399
3866 | 34.398
3867 | 34.398
3868 | 34.398
3869 | 34.397
3870 | 34.395
3871 | 34.393
3872 | 34.391
3873 | 34.389
3874 | 34.383
3875 | 34.381
3876 | 34.377
3877 | 34.376
3878 | 34.372
3879 | 34.372
3880 | 34.37
3881 | 34.367
3882 | 34.364
3883 | 34.36
3884 | 34.355
3885 | 34.354
3886 | 34.354
3887 | 34.35
3888 | 34.345
3889 | 34.344
3890 | 34.337
3891 | 34.336
3892 | 34.336
3893 | 34.332
3894 | 34.326
3895 | 34.321
3896 | 34.32
3897 | 34.32
3898 | 34.316
3899 | 34.313
3900 | 34.313
3901 | 34.313
3902 | 34.312
3903 | 34.309
3904 | 34.309
3905 | 34.307
3906 | 34.305
3907 | 34.301
3908 | 34.301
3909 | 34.3
3910 | 34.299
3911 | 34.297
3912 | 34.296
3913 | 34.296
3914 | 34.292
3915 | 34.289
3916 | 34.282
3917 | 34.281
3918 | 34.278
3919 | 34.277
3920 | 34.276
3921 | 34.276
3922 | 34.276
3923 | 34.275
3924 | 34.275
3925 | 34.274
3926 | 34.274
3927 | 34.271
3928 | 34.271
3929 | 34.267
3930 | 34.267
3931 | 34.263
3932 | 34.261
3933 | 34.258
3934 | 34.255
3935 | 34.253
3936 | 34.251
3937 | 34.25
3938 | 34.249
3939 | 34.247
3940 | 34.247
3941 | 34.244
3942 | 34.244
3943 | 34.243
3944 | 34.242
3945 | 34.24
3946 | 34.235
3947 | 34.235
3948 | 34.233
3949 | 34.232
3950 | 34.231
3951 | 34.225
3952 | 34.222
3953 | 34.221
3954 | 34.219
3955 | 34.21
3956 | 34.208
3957 | 34.207
3958 | 34.207
3959 | 34.203
3960 | 34.203
3961 | 34.199
3962 | 34.198
3963 | 34.198
3964 | 34.196
3965 | 34.194
3966 | 34.192
3967 | 34.192
3968 | 34.19
3969 | 34.19
3970 | 34.189
3971 | 34.189
3972 | 34.184
3973 | 34.181
3974 | 34.179
3975 | 34.175
3976 | 34.175
3977 | 34.174
3978 | 34.174
3979 | 34.173
3980 | 34.171
3981 | 34.171
3982 | 34.169
3983 | 34.166
3984 | 34.166
3985 | 34.166
3986 | 34.165
3987 | 34.165
3988 | 34.162
3989 | 34.16
3990 | 34.16
3991 | 34.159
3992 | 34.157
3993 | 34.156
3994 | 34.156
3995 | 34.155
3996 | 34.153
3997 | 34.15
3998 | 34.15
3999 | 34.148
4000 | 34.143
4001 | 34.142
4002 | 34.138
4003 | 34.136
4004 | 34.132
4005 | 34.13
4006 | 34.129
4007 | 34.129
4008 | 34.125
4009 | 34.121
4010 | 34.12
4011 | 34.119
4012 | 34.114
4013 | 34.11
4014 | 34.109
4015 | 34.108
4016 | 34.107
4017 | 34.104
4018 | 34.099
4019 | 34.098
4020 | 34.098
4021 | 34.095
4022 | 34.092
4023 | 34.092
4024 | 34.09
4025 | 34.085
4026 | 34.083
4027 | 34.082
4028 | 34.081
4029 | 34.077
4030 | 34.076
4031 | 34.075
4032 | 34.072
4033 | 34.072
4034 | 34.067
4035 | 34.066
4036 | 34.066
4037 | 34.065
4038 | 34.058
4039 | 34.058
4040 | 34.057
4041 | 34.056
4042 | 34.055
4043 | 34.054
4044 | 34.052
4045 | 34.052
4046 | 34.052
4047 | 34.051
4048 | 34.045
4049 | 34.044
4050 | 34.044
4051 | 34.043
4052 | 34.041
4053 | 34.041
4054 | 34.039
4055 | 34.038
4056 | 34.037
4057 | 34.035
4058 | 34.035
4059 | 34.033
4060 | 34.033
4061 | 34.032
4062 | 34.029
4063 | 34.029
4064 | 34.028
4065 | 34.027
4066 | 34.026
4067 | 34.025
4068 | 34.022
4069 | 34.019
4070 | 34.019
4071 | 34.017
4072 | 34.017
4073 | 34.016
4074 | 34.016
4075 | 34.015
4076 | 34.015
4077 | 34.013
4078 | 34.011
4079 | 34.01
4080 | 34.009
4081 | 34.005
4082 | 34
4083 | 33.998
4084 | 33.991
4085 | 33.989
4086 | 33.987
4087 | 33.986
4088 | 33.984
4089 | 33.983
4090 | 33.982
4091 | 33.98
4092 | 33.979
4093 | 33.979
4094 | 33.978
4095 | 33.977
4096 | 33.976
4097 | 33.971
4098 | 33.971
4099 | 33.969
4100 | 33.969
4101 | 33.968
4102 | 33.968
4103 | 33.965
4104 | 33.963
4105 | 33.963
4106 | 33.962
4107 | 33.96
4108 | 33.958
4109 | 33.955
4110 | 33.954
4111 | 33.952
4112 | 33.95
4113 | 33.948
4114 | 33.947
4115 | 33.947
4116 | 33.942
4117 | 33.94
4118 | 33.939
4119 | 33.936
4120 | 33.931
4121 | 33.92
4122 | 33.919
4123 | 33.915
4124 | 33.914
4125 | 33.911
4126 | 33.91
4127 | 33.909
4128 | 33.907
4129 | 33.906
4130 | 33.905
4131 | 33.904
4132 | 33.9
4133 | 33.899
4134 | 33.897
4135 | 33.896
4136 | 33.895
4137 | 33.894
4138 | 33.894
4139 | 33.894
4140 | 33.893
4141 | 33.892
4142 | 33.891
4143 | 33.888
4144 | 33.888
4145 | 33.887
4146 | 33.886
4147 | 33.886
4148 | 33.881
4149 | 33.88
4150 | 33.873
4151 | 33.872
4152 | 33.871
4153 | 33.868
4154 | 33.867
4155 | 33.866
4156 | 33.863
4157 | 33.861
4158 | 33.859
4159 | 33.859
4160 | 33.856
4161 | 33.854
4162 | 33.853
4163 | 33.851
4164 | 33.847
4165 | 33.847
4166 | 33.847
4167 | 33.843
4168 | 33.843
4169 | 33.831
4170 | 33.829
4171 | 33.823
4172 | 33.821
4173 | 33.817
4174 | 33.815
4175 | 33.814
4176 | 33.813
4177 | 33.812
4178 | 33.808
4179 | 33.804
4180 | 33.8
4181 | 33.797
4182 | 33.792
4183 | 33.79
4184 | 33.785
4185 | 33.785
4186 | 33.783
4187 | 33.781
4188 | 33.78
4189 | 33.78
4190 | 33.778
4191 | 33.777
4192 | 33.774
4193 | 33.773
4194 | 33.766
4195 | 33.766
4196 | 33.765
4197 | 33.76
4198 | 33.76
4199 | 33.757
4200 | 33.757
4201 | 33.754
4202 | 33.753
4203 | 33.753
4204 | 33.753
4205 | 33.752
4206 | 33.751
4207 | 33.749
4208 | 33.748
4209 | 33.743
4210 | 33.742
4211 | 33.738
4212 | 33.731
4213 | 33.731
4214 | 33.731
4215 | 33.73
4216 | 33.727
4217 | 33.724
4218 | 33.724
4219 | 33.723
4220 | 33.72
4221 | 33.719
4222 | 33.713
4223 | 33.709
4224 | 33.705
4225 | 33.704
4226 | 33.701
4227 | 33.7
4228 | 33.699
4229 | 33.698
4230 | 33.697
4231 | 33.697
4232 | 33.693
4233 | 33.692
4234 | 33.691
4235 | 33.69
4236 | 33.69
4237 | 33.69
4238 | 33.69
4239 | 33.688
4240 | 33.678
4241 | 33.676
4242 | 33.674
4243 | 33.672
4244 | 33.67
4245 | 33.669
4246 | 33.666
4247 | 33.665
4248 | 33.664
4249 | 33.663
4250 | 33.662
4251 | 33.661
4252 | 33.658
4253 | 33.655
4254 | 33.654
4255 | 33.654
4256 | 33.651
4257 | 33.648
4258 | 33.647
4259 | 33.646
4260 | 33.646
4261 | 33.646
4262 | 33.644
4263 | 33.644
4264 | 33.644
4265 | 33.641
4266 | 33.641
4267 | 33.637
4268 | 33.633
4269 | 33.631
4270 | 33.63
4271 | 33.628
4272 | 33.628
4273 | 33.624
4274 | 33.623
4275 | 33.622
4276 | 33.621
4277 | 33.618
4278 | 33.618
4279 | 33.617
4280 | 33.617
4281 | 33.614
4282 | 33.612
4283 | 33.606
4284 | 33.601
4285 | 33.601
4286 | 33.599
4287 | 33.593
4288 | 33.588
4289 | 33.584
4290 | 33.583
4291 | 33.581
4292 | 33.581
4293 | 33.581
4294 | 33.578
4295 | 33.578
4296 | 33.577
4297 | 33.576
4298 | 33.574
4299 | 33.574
4300 | 33.571
4301 | 33.564
4302 | 33.563
4303 | 33.561
4304 | 33.56
4305 | 33.556
4306 | 33.555
4307 | 33.555
4308 | 33.555
4309 | 33.554
4310 | 33.554
4311 | 33.553
4312 | 33.552
4313 | 33.545
4314 | 33.544
4315 | 33.542
4316 | 33.539
4317 | 33.538
4318 | 33.538
4319 | 33.535
4320 | 33.535
4321 | 33.533
4322 | 33.531
4323 | 33.526
4324 | 33.524
4325 | 33.521
4326 | 33.519
4327 | 33.513
4328 | 33.513
4329 | 33.512
4330 | 33.51
4331 | 33.509
4332 | 33.509
4333 | 33.508
4334 | 33.507
4335 | 33.504
4336 | 33.5
4337 | 33.499
4338 | 33.497
4339 | 33.495
4340 | 33.495
4341 | 33.492
4342 | 33.488
4343 | 33.487
4344 | 33.483
4345 | 33.479
4346 | 33.479
4347 | 33.477
4348 | 33.477
4349 | 33.474
4350 | 33.471
4351 | 33.468
4352 | 33.466
4353 | 33.461
4354 | 33.458
4355 | 33.457
4356 | 33.456
4357 | 33.455
4358 | 33.454
4359 | 33.454
4360 | 33.454
4361 | 33.451
4362 | 33.449
4363 | 33.445
4364 | 33.444
4365 | 33.439
4366 | 33.439
4367 | 33.438
4368 | 33.437
4369 | 33.437
4370 | 33.434
4371 | 33.426
4372 | 33.422
4373 | 33.422
4374 | 33.418
4375 | 33.416
4376 | 33.414
4377 | 33.412
4378 | 33.412
4379 | 33.403
4380 | 33.402
4381 | 33.4
4382 | 33.4
4383 | 33.397
4384 | 33.396
4385 | 33.395
4386 | 33.395
4387 | 33.391
4388 | 33.391
4389 | 33.391
4390 | 33.389
4391 | 33.387
4392 | 33.385
4393 | 33.38
4394 | 33.379
4395 | 33.379
4396 | 33.377
4397 | 33.372
4398 | 33.372
4399 | 33.371
4400 | 33.368
4401 | 33.365
4402 | 33.362
4403 | 33.361
4404 | 33.359
4405 | 33.35
4406 | 33.349
4407 | 33.348
4408 | 33.347
4409 | 33.344
4410 | 33.343
4411 | 33.342
4412 | 33.34
4413 | 33.337
4414 | 33.334
4415 | 33.334
4416 | 33.334
4417 | 33.332
4418 | 33.325
4419 | 33.321
4420 | 33.318
4421 | 33.316
4422 | 33.316
4423 | 33.314
4424 | 33.312
4425 | 33.312
4426 | 33.311
4427 | 33.304
4428 | 33.3
4429 | 33.296
4430 | 33.295
4431 | 33.294
4432 | 33.294
4433 | 33.292
4434 | 33.291
4435 | 33.288
4436 | 33.287
4437 | 33.285
4438 | 33.283
4439 | 33.283
4440 | 33.282
4441 | 33.28
4442 | 33.277
4443 | 33.276
4444 | 33.275
4445 | 33.274
4446 | 33.272
4447 | 33.269
4448 | 33.269
4449 | 33.262
4450 | 33.261
4451 | 33.261
4452 | 33.261
4453 | 33.261
4454 | 33.259
4455 | 33.258
4456 | 33.258
4457 | 33.257
4458 | 33.256
4459 | 33.256
4460 | 33.256
4461 | 33.254
4462 | 33.253
4463 | 33.251
4464 | 33.249
4465 | 33.248
4466 | 33.246
4467 | 33.245
4468 | 33.244
4469 | 33.242
4470 | 33.24
4471 | 33.24
4472 | 33.24
4473 | 33.239
4474 | 33.239
4475 | 33.237
4476 | 33.236
4477 | 33.235
4478 | 33.231
4479 | 33.23
4480 | 33.229
4481 | 33.226
4482 | 33.225
4483 | 33.225
4484 | 33.225
4485 | 33.223
4486 | 33.223
4487 | 33.221
4488 | 33.22
4489 | 33.217
4490 | 33.216
4491 | 33.216
4492 | 33.216
4493 | 33.21
4494 | 33.209
4495 | 33.208
4496 | 33.208
4497 | 33.207
4498 | 33.204
4499 | 33.202
4500 | 33.2
4501 | 33.199
4502 | 33.197
4503 | 33.193
4504 | 33.193
4505 | 33.193
4506 | 33.192
4507 | 33.191
4508 | 33.19
4509 | 33.188
4510 | 33.188
4511 | 33.184
4512 | 33.184
4513 | 33.181
4514 | 33.179
4515 | 33.177
4516 | 33.176
4517 | 33.172
4518 | 33.17
4519 | 33.169
4520 | 33.168
4521 | 33.168
4522 | 33.165
4523 | 33.162
4524 | 33.159
4525 | 33.158
4526 | 33.158
4527 | 33.154
4528 | 33.153
4529 | 33.151
4530 | 33.149
4531 | 33.141
4532 | 33.141
4533 | 33.14
4534 | 33.139
4535 | 33.139
4536 | 33.138
4537 | 33.135
4538 | 33.135
4539 | 33.134
4540 | 33.134
4541 | 33.129
4542 | 33.128
4543 | 33.126
4544 | 33.123
4545 | 33.121
4546 | 33.118
4547 | 33.115
4548 | 33.115
4549 | 33.113
4550 | 33.111
4551 | 33.11
4552 | 33.11
4553 | 33.108
4554 | 33.106
4555 | 33.104
4556 | 33.104
4557 | 33.104
4558 | 33.101
4559 | 33.097
4560 | 33.096
4561 | 33.093
4562 | 33.092
4563 | 33.089
4564 | 33.088
4565 | 33.088
4566 | 33.085
4567 | 33.083
4568 | 33.081
4569 | 33.081
4570 | 33.081
4571 | 33.078
4572 | 33.077
4573 | 33.074
4574 | 33.074
4575 | 33.073
4576 | 33.073
4577 | 33.067
4578 | 33.067
4579 | 33.066
4580 | 33.066
4581 | 33.064
4582 | 33.063
4583 | 33.058
4584 | 33.057
4585 | 33.057
4586 | 33.057
4587 | 33.054
4588 | 33.054
4589 | 33.054
4590 | 33.053
4591 | 33.052
4592 | 33.051
4593 | 33.05
4594 | 33.049
4595 | 33.049
4596 | 33.049
4597 | 33.043
4598 | 33.04
4599 | 33.04
4600 | 33.039
4601 | 33.036
4602 | 33.035
4603 | 33.033
4604 | 33.033
4605 | 33.033
4606 | 33.029
4607 | 33.029
4608 | 33.028
4609 | 33.022
4610 | 33.021
4611 | 33.017
4612 | 33.017
4613 | 33.015
4614 | 33.015
4615 | 33.013
4616 | 33.012
4617 | 33.009
4618 | 33.008
4619 | 33.007
4620 | 33.007
4621 | 33.006
4622 | 33.005
4623 | 33.002
4624 | 33
4625 | 33
4626 | 32.998
4627 | 32.997
4628 | 32.996
4629 | 32.994
4630 | 32.993
4631 | 32.993
4632 | 32.99
4633 | 32.984
4634 | 32.982
4635 | 32.975
4636 | 32.97
4637 | 32.97
4638 | 32.968
4639 | 32.965
4640 | 32.965
4641 | 32.962
4642 | 32.96
4643 | 32.96
4644 | 32.96
4645 | 32.959
4646 | 32.955
4647 | 32.953
4648 | 32.947
4649 | 32.944
4650 | 32.944
4651 | 32.944
4652 | 32.937
4653 | 32.937
4654 | 32.935
4655 | 32.934
4656 | 32.933
4657 | 32.933
4658 | 32.93
4659 | 32.929
4660 | 32.927
4661 | 32.925
4662 | 32.924
4663 | 32.924
4664 | 32.924
4665 | 32.924
4666 | 32.921
4667 | 32.919
4668 | 32.919
4669 | 32.917
4670 | 32.917
4671 | 32.915
4672 | 32.913
4673 | 32.912
4674 | 32.91
4675 | 32.91
4676 | 32.91
4677 | 32.909
4678 | 32.905
4679 | 32.904
4680 | 32.902
4681 | 32.896
4682 | 32.894
4683 | 32.894
4684 | 32.893
4685 | 32.893
4686 | 32.893
4687 | 32.892
4688 | 32.89
4689 | 32.888
4690 | 32.884
4691 | 32.883
4692 | 32.88
4693 | 32.88
4694 | 32.88
4695 | 32.879
4696 | 32.874
4697 | 32.868
4698 | 32.862
4699 | 32.86
4700 | 32.86
4701 | 32.86
4702 | 32.858
4703 | 32.857
4704 | 32.857
4705 | 32.855
4706 | 32.854
4707 | 32.853
4708 | 32.853
4709 | 32.848
4710 | 32.848
4711 | 32.847
4712 | 32.847
4713 | 32.845
4714 | 32.845
4715 | 32.844
4716 | 32.844
4717 | 32.842
4718 | 32.841
4719 | 32.837
4720 | 32.837
4721 | 32.832
4722 | 32.831
4723 | 32.828
4724 | 32.826
4725 | 32.826
4726 | 32.825
4727 | 32.825
4728 | 32.821
4729 | 32.82
4730 | 32.814
4731 | 32.814
4732 | 32.814
4733 | 32.812
4734 | 32.811
4735 | 32.811
4736 | 32.808
4737 | 32.808
4738 | 32.806
4739 | 32.806
4740 | 32.805
4741 | 32.805
4742 | 32.805
4743 | 32.805
4744 | 32.804
4745 | 32.804
4746 | 32.803
4747 | 32.803
4748 | 32.802
4749 | 32.8
4750 | 32.798
4751 | 32.798
4752 | 32.796
4753 | 32.794
4754 | 32.791
4755 | 32.79
4756 | 32.789
4757 | 32.789
4758 | 32.787
4759 | 32.786
4760 | 32.785
4761 | 32.779
4762 | 32.777
4763 | 32.777
4764 | 32.774
4765 | 32.772
4766 | 32.771
4767 | 32.769
4768 | 32.768
4769 | 32.766
4770 | 32.765
4771 | 32.764
4772 | 32.762
4773 | 32.76
4774 | 32.756
4775 | 32.755
4776 | 32.748
4777 | 32.746
4778 | 32.746
4779 | 32.745
4780 | 32.745
4781 | 32.744
4782 | 32.744
4783 | 32.743
4784 | 32.742
4785 | 32.742
4786 | 32.739
4787 | 32.739
4788 | 32.739
4789 | 32.738
4790 | 32.738
4791 | 32.733
4792 | 32.73
4793 | 32.729
4794 | 32.728
4795 | 32.728
4796 | 32.727
4797 | 32.727
4798 | 32.727
4799 | 32.726
4800 | 32.725
4801 | 32.723
4802 | 32.718
4803 | 32.718
4804 | 32.716
4805 | 32.715
4806 | 32.714
4807 | 32.711
4808 | 32.711
4809 | 32.71
4810 | 32.708
4811 | 32.706
4812 | 32.705
4813 | 32.705
4814 | 32.705
4815 | 32.704
4816 | 32.703
4817 | 32.7
4818 | 32.698
4819 | 32.697
4820 | 32.693
4821 | 32.693
4822 | 32.691
4823 | 32.688
4824 | 32.687
4825 | 32.687
4826 | 32.685
4827 | 32.684
4828 | 32.681
4829 | 32.677
4830 | 32.674
4831 | 32.674
4832 | 32.673
4833 | 32.669
4834 | 32.663
4835 | 32.658
4836 | 32.656
4837 | 32.655
4838 | 32.654
4839 | 32.649
4840 | 32.648
4841 | 32.648
4842 | 32.648
4843 | 32.647
4844 | 32.646
4845 | 32.645
4846 | 32.645
4847 | 32.641
4848 | 32.641
4849 | 32.639
4850 | 32.637
4851 | 32.635
4852 | 32.634
4853 | 32.634
4854 | 32.63
4855 | 32.629
4856 | 32.626
4857 | 32.625
4858 | 32.625
4859 | 32.624
4860 | 32.624
4861 | 32.622
4862 | 32.617
4863 | 32.617
4864 | 32.615
4865 | 32.608
4866 | 32.608
4867 | 32.608
4868 | 32.608
4869 | 32.602
4870 | 32.601
4871 | 32.599
4872 | 32.599
4873 | 32.598
4874 | 32.595
4875 | 32.594
4876 | 32.593
4877 | 32.59
4878 | 32.59
4879 | 32.589
4880 | 32.588
4881 | 32.588
4882 | 32.587
4883 | 32.586
4884 | 32.583
4885 | 32.581
4886 | 32.581
4887 | 32.579
4888 | 32.579
4889 | 32.579
4890 | 32.575
4891 | 32.575
4892 | 32.574
4893 | 32.57
4894 | 32.567
4895 | 32.565
4896 | 32.565
4897 | 32.564
4898 | 32.562
4899 | 32.559
4900 | 32.558
4901 | 32.554
4902 | 32.551
4903 | 32.551
4904 | 32.55
4905 | 32.549
4906 | 32.547
4907 | 32.547
4908 | 32.546
4909 | 32.544
4910 | 32.544
4911 | 32.543
4912 | 32.541
4913 | 32.54
4914 | 32.538
4915 | 32.534
4916 | 32.534
4917 | 32.534
4918 | 32.531
4919 | 32.529
4920 | 32.528
4921 | 32.528
4922 | 32.523
4923 | 32.521
4924 | 32.521
4925 | 32.521
4926 | 32.517
4927 | 32.516
4928 | 32.514
4929 | 32.512
4930 | 32.511
4931 | 32.507
4932 | 32.507
4933 | 32.507
4934 | 32.506
4935 | 32.504
4936 | 32.503
4937 | 32.502
4938 | 32.501
4939 | 32.499
4940 | 32.498
4941 | 32.488
4942 | 32.488
4943 | 32.488
4944 | 32.487
4945 | 32.485
4946 | 32.485
4947 | 32.484
4948 | 32.483
4949 | 32.483
4950 | 32.482
4951 | 32.48
4952 | 32.477
4953 | 32.476
4954 | 32.474
4955 | 32.469
4956 | 32.467
4957 | 32.466
4958 | 32.465
4959 | 32.464
4960 | 32.462
4961 | 32.461
4962 | 32.459
4963 | 32.459
4964 | 32.455
4965 | 32.454
4966 | 32.449
4967 | 32.444
4968 | 32.443
4969 | 32.442
4970 | 32.44
4971 | 32.438
4972 | 32.436
4973 | 32.436
4974 | 32.431
4975 | 32.43
4976 | 32.428
4977 | 32.427
4978 | 32.426
4979 | 32.426
4980 | 32.425
4981 | 32.424
4982 | 32.421
4983 | 32.421
4984 | 32.419
4985 | 32.415
4986 | 32.414
4987 | 32.412
4988 | 32.411
4989 | 32.409
4990 | 32.408
4991 | 32.407
4992 | 32.404
4993 | 32.404
4994 | 32.401
4995 | 32.4
4996 | 32.398
4997 | 32.397
4998 | 32.395
4999 | 32.391
5000 | 32.388
5001 | 32.388
5002 | 32.387
5003 | 32.385
5004 | 32.383
5005 | 32.382
5006 | 32.377
5007 | 32.376
5008 | 32.376
5009 | 32.375
5010 | 32.373
5011 | 32.372
5012 | 32.37
5013 | 32.37
5014 | 32.37
5015 | 32.37
5016 | 32.368
5017 | 32.368
5018 | 32.367
5019 | 32.366
5020 | 32.364
5021 | 32.363
5022 | 32.361
5023 | 32.36
5024 | 32.356
5025 | 32.356
5026 | 32.355
5027 | 32.354
5028 | 32.353
5029 | 32.351
5030 | 32.349
5031 | 32.347
5032 | 32.346
5033 | 32.345
5034 | 32.344
5035 | 32.342
5036 | 32.34
5037 | 32.34
5038 | 32.338
5039 | 32.337
5040 | 32.337
5041 | 32.335
5042 | 32.331
5043 | 32.329
5044 | 32.328
5045 | 32.327
5046 | 32.327
5047 | 32.321
5048 | 32.32
5049 | 32.318
5050 | 32.316
5051 | 32.312
5052 | 32.31
5053 | 32.308
5054 | 32.308
5055 | 32.305
5056 | 32.305
5057 | 32.305
5058 | 32.3
5059 | 32.3
5060 | 32.299
5061 | 32.297
5062 | 32.297
5063 | 32.294
5064 | 32.292
5065 | 32.291
5066 | 32.29
5067 | 32.29
5068 | 32.289
5069 | 32.288
5070 | 32.288
5071 | 32.287
5072 | 32.282
5073 | 32.273
5074 | 32.273
5075 | 32.273
5076 | 32.272
5077 | 32.271
5078 | 32.267
5079 | 32.264
5080 | 32.262
5081 | 32.26
5082 | 32.253
5083 | 32.252
5084 | 32.243
5085 | 32.24
5086 | 32.239
5087 | 32.236
5088 | 32.235
5089 | 32.234
5090 | 32.229
5091 | 32.227
5092 | 32.223
5093 | 32.219
5094 | 32.217
5095 | 32.217
5096 | 32.211
5097 | 32.21
5098 | 32.209
5099 | 32.207
5100 | 32.207
5101 | 32.205
5102 | 32.205
5103 | 32.205
5104 | 32.203
5105 | 32.202
5106 | 32.202
5107 | 32.2
5108 | 32.199
5109 | 32.198
5110 | 32.197
5111 | 32.196
5112 | 32.195
5113 | 32.192
5114 | 32.19
5115 | 32.187
5116 | 32.187
5117 | 32.184
5118 | 32.181
5119 | 32.18
5120 | 32.18
5121 | 32.179
5122 | 32.175
5123 | 32.173
5124 | 32.17
5125 | 32.169
5126 | 32.167
5127 | 32.166
5128 | 32.165
5129 | 32.163
5130 | 32.16
5131 | 32.159
5132 | 32.156
5133 | 32.155
5134 | 32.15
5135 | 32.15
5136 | 32.15
5137 | 32.15
5138 | 32.148
5139 | 32.148
5140 | 32.148
5141 | 32.146
5142 | 32.145
5143 | 32.144
5144 | 32.144
5145 | 32.142
5146 | 32.14
5147 | 32.137
5148 | 32.137
5149 | 32.136
5150 | 32.135
5151 | 32.135
5152 | 32.133
5153 | 32.132
5154 | 32.13
5155 | 32.13
5156 | 32.129
5157 | 32.128
5158 | 32.126
5159 | 32.123
5160 | 32.122
5161 | 32.118
5162 | 32.117
5163 | 32.116
5164 | 32.116
5165 | 32.111
5166 | 32.111
5167 | 32.108
5168 | 32.106
5169 | 32.106
5170 | 32.101
5171 | 32.101
5172 | 32.099
5173 | 32.098
5174 | 32.098
5175 | 32.096
5176 | 32.096
5177 | 32.094
5178 | 32.093
5179 | 32.093
5180 | 32.092
5181 | 32.091
5182 | 32.089
5183 | 32.089
5184 | 32.087
5185 | 32.085
5186 | 32.085
5187 | 32.085
5188 | 32.084
5189 | 32.082
5190 | 32.082
5191 | 32.081
5192 | 32.078
5193 | 32.076
5194 | 32.073
5195 | 32.069
5196 | 32.069
5197 | 32.067
5198 | 32.06
5199 | 32.059
5200 | 32.057
5201 | 32.055
5202 | 32.048
5203 | 32.048
5204 | 32.047
5205 | 32.046
5206 | 32.046
5207 | 32.045
5208 | 32.043
5209 | 32.043
5210 | 32.042
5211 | 32.042
5212 | 32.042
5213 | 32.039
5214 | 32.039
5215 | 32.037
5216 | 32.037
5217 | 32.036
5218 | 32.035
5219 | 32.035
5220 | 32.034
5221 | 32.032
5222 | 32.032
5223 | 32.032
5224 | 32.03
5225 | 32.03
5226 | 32.027
5227 | 32.026
5228 | 32.022
5229 | 32.02
5230 | 32.018
5231 | 32.017
5232 | 32.014
5233 | 32.011
5234 | 32.011
5235 | 32.009
5236 | 32.009
5237 | 32.008
5238 | 32.008
5239 | 32.007
5240 | 32.007
5241 | 32.007
5242 | 32.007
5243 | 32.007
5244 | 32.006
5245 | 32.006
5246 | 32.005
5247 | 32.002
5248 | 32.002
5249 | 32.002
5250 | 32.001
5251 | 31.997
5252 | 31.996
5253 | 31.995
5254 | 31.995
5255 | 31.991
5256 | 31.99
5257 | 31.989
5258 | 31.989
5259 | 31.988
5260 | 31.985
5261 | 31.981
5262 | 31.979
5263 | 31.979
5264 | 31.976
5265 | 31.975
5266 | 31.975
5267 | 31.974
5268 | 31.972
5269 | 31.971
5270 | 31.97
5271 | 31.969
5272 | 31.968
5273 | 31.968
5274 | 31.967
5275 | 31.965
5276 | 31.964
5277 | 31.962
5278 | 31.962
5279 | 31.961
5280 | 31.96
5281 | 31.958
5282 | 31.954
5283 | 31.953
5284 | 31.953
5285 | 31.952
5286 | 31.952
5287 | 31.951
5288 | 31.949
5289 | 31.948
5290 | 31.947
5291 | 31.945
5292 | 31.945
5293 | 31.943
5294 | 31.939
5295 | 31.938
5296 | 31.936
5297 | 31.936
5298 | 31.935
5299 | 31.933
5300 | 31.932
5301 | 31.931
5302 | 31.927
5303 | 31.926
5304 | 31.923
5305 | 31.922
5306 | 31.919
5307 | 31.918
5308 | 31.916
5309 | 31.914
5310 | 31.912
5311 | 31.912
5312 | 31.91
5313 | 31.904
5314 | 31.904
5315 | 31.902
5316 | 31.9
5317 | 31.898
5318 | 31.897
5319 | 31.896
5320 | 31.887
5321 | 31.886
5322 | 31.886
5323 | 31.884
5324 | 31.883
5325 | 31.882
5326 | 31.88
5327 | 31.879
5328 | 31.879
5329 | 31.879
5330 | 31.879
5331 | 31.874
5332 | 31.874
5333 | 31.873
5334 | 31.869
5335 | 31.865
5336 | 31.862
5337 | 31.862
5338 | 31.861
5339 | 31.861
5340 | 31.858
5341 | 31.857
5342 | 31.857
5343 | 31.857
5344 | 31.855
5345 | 31.855
5346 | 31.855
5347 | 31.855
5348 | 31.855
5349 | 31.851
5350 | 31.85
5351 | 31.848
5352 | 31.847
5353 | 31.844
5354 | 31.843
5355 | 31.837
5356 | 31.837
5357 | 31.837
5358 | 31.837
5359 | 31.836
5360 | 31.834
5361 | 31.832
5362 | 31.832
5363 | 31.831
5364 | 31.827
5365 | 31.826
5366 | 31.824
5367 | 31.821
5368 | 31.82
5369 | 31.819
5370 | 31.816
5371 | 31.815
5372 | 31.814
5373 | 31.814
5374 | 31.814
5375 | 31.813
5376 | 31.811
5377 | 31.809
5378 | 31.807
5379 | 31.802
5380 | 31.801
5381 | 31.799
5382 | 31.797
5383 | 31.796
5384 | 31.793
5385 | 31.792
5386 | 31.789
5387 | 31.787
5388 | 31.787
5389 | 31.787
5390 | 31.785
5391 | 31.784
5392 | 31.784
5393 | 31.782
5394 | 31.78
5395 | 31.777
5396 | 31.776
5397 | 31.774
5398 | 31.774
5399 | 31.771
5400 | 31.77
5401 | 31.77
5402 | 31.766
5403 | 31.763
5404 | 31.763
5405 | 31.763
5406 | 31.759
5407 | 31.759
5408 | 31.757
5409 | 31.756
5410 | 31.753
5411 | 31.752
5412 | 31.75
5413 | 31.748
5414 | 31.748
5415 | 31.747
5416 | 31.747
5417 | 31.746
5418 | 31.746
5419 | 31.745
5420 | 31.744
5421 | 31.744
5422 | 31.743
5423 | 31.741
5424 | 31.74
5425 | 31.737
5426 | 31.735
5427 | 31.735
5428 | 31.734
5429 | 31.732
5430 | 31.729
5431 | 31.729
5432 | 31.727
5433 | 31.726
5434 | 31.725
5435 | 31.725
5436 | 31.723
5437 | 31.722
5438 | 31.722
5439 | 31.722
5440 | 31.72
5441 | 31.718
5442 | 31.713
5443 | 31.709
5444 | 31.707
5445 | 31.706
5446 | 31.705
5447 | 31.705
5448 | 31.704
5449 | 31.704
5450 | 31.701
5451 | 31.7
5452 | 31.7
5453 | 31.698
5454 | 31.697
5455 | 31.697
5456 | 31.695
5457 | 31.694
5458 | 31.69
5459 | 31.688
5460 | 31.686
5461 | 31.684
5462 | 31.684
5463 | 31.684
5464 | 31.683
5465 | 31.683
5466 | 31.681
5467 | 31.681
5468 | 31.678
5469 | 31.677
5470 | 31.676
5471 | 31.675
5472 | 31.673
5473 | 31.671
5474 | 31.671
5475 | 31.667
5476 | 31.667
5477 | 31.665
5478 | 31.663
5479 | 31.661
5480 | 31.661
5481 | 31.661
5482 | 31.658
5483 | 31.658
5484 | 31.658
5485 | 31.656
5486 | 31.654
5487 | 31.653
5488 | 31.652
5489 | 31.652
5490 | 31.651
5491 | 31.65
5492 | 31.648
5493 | 31.647
5494 | 31.634
5495 | 31.632
5496 | 31.631
5497 | 31.629
5498 | 31.623
5499 | 31.622
5500 | 31.619
5501 | 31.617
5502 | 31.615
5503 | 31.615
5504 | 31.614
5505 | 31.612
5506 | 31.611
5507 | 31.61
5508 | 31.608
5509 | 31.606
5510 | 31.606
5511 | 31.605
5512 | 31.605
5513 | 31.602
5514 | 31.601
5515 | 31.6
5516 | 31.598
5517 | 31.593
5518 | 31.591
5519 | 31.59
5520 | 31.589
5521 | 31.588
5522 | 31.588
5523 | 31.587
5524 | 31.586
5525 | 31.585
5526 | 31.584
5527 | 31.584
5528 | 31.583
5529 | 31.583
5530 | 31.581
5531 | 31.58
5532 | 31.579
5533 | 31.577
5534 | 31.569
5535 | 31.568
5536 | 31.568
5537 | 31.562
5538 | 31.562
5539 | 31.559
5540 | 31.559
5541 | 31.558
5542 | 31.555
5543 | 31.555
5544 | 31.552
5545 | 31.552
5546 | 31.55
5547 | 31.548
5548 | 31.547
5549 | 31.546
5550 | 31.546
5551 | 31.545
5552 | 31.542
5553 | 31.539
5554 | 31.538
5555 | 31.538
5556 | 31.536
5557 | 31.536
5558 | 31.534
5559 | 31.53
5560 | 31.529
5561 | 31.528
5562 | 31.525
5563 | 31.521
5564 | 31.52
5565 | 31.519
5566 | 31.518
5567 | 31.518
5568 | 31.517
5569 | 31.516
5570 | 31.513
5571 | 31.512
5572 | 31.509
5573 | 31.508
5574 | 31.507
5575 | 31.506
5576 | 31.505
5577 | 31.505
5578 | 31.503
5579 | 31.503
5580 | 31.503
5581 | 31.501
5582 | 31.501
5583 | 31.5
5584 | 31.499
5585 | 31.499
5586 | 31.498
5587 | 31.497
5588 | 31.497
5589 | 31.491
5590 | 31.49
5591 | 31.488
5592 | 31.488
5593 | 31.487
5594 | 31.487
5595 | 31.487
5596 | 31.487
5597 | 31.482
5598 | 31.481
5599 | 31.479
5600 | 31.476
5601 | 31.475
5602 | 31.474
5603 | 31.473
5604 | 31.472
5605 | 31.468
5606 | 31.468
5607 | 31.463
5608 | 31.463
5609 | 31.461
5610 | 31.457
5611 | 31.457
5612 | 31.455
5613 | 31.455
5614 | 31.455
5615 | 31.455
5616 | 31.453
5617 | 31.452
5618 | 31.45
5619 | 31.45
5620 | 31.45
5621 | 31.449
5622 | 31.447
5623 | 31.446
5624 | 31.445
5625 | 31.445
5626 | 31.444
5627 | 31.443
5628 | 31.443
5629 | 31.442
5630 | 31.441
5631 | 31.44
5632 | 31.439
5633 | 31.438
5634 | 31.438
5635 | 31.437
5636 | 31.436
5637 | 31.435
5638 | 31.433
5639 | 31.433
5640 | 31.433
5641 | 31.432
5642 | 31.432
5643 | 31.431
5644 | 31.431
5645 | 31.43
5646 | 31.429
5647 | 31.429
5648 | 31.427
5649 | 31.427
5650 | 31.424
5651 | 31.422
5652 | 31.419
5653 | 31.418
5654 | 31.418
5655 | 31.413
5656 | 31.413
5657 | 31.412
5658 | 31.412
5659 | 31.41
5660 | 31.409
5661 | 31.408
5662 | 31.405
5663 | 31.404
5664 | 31.402
5665 | 31.402
5666 | 31.402
5667 | 31.401
5668 | 31.4
5669 | 31.396
5670 | 31.395
5671 | 31.394
5672 | 31.393
5673 | 31.393
5674 | 31.392
5675 | 31.392
5676 | 31.391
5677 | 31.39
5678 | 31.389
5679 | 31.388
5680 | 31.387
5681 | 31.382
5682 | 31.38
5683 | 31.377
5684 | 31.377
5685 | 31.376
5686 | 31.375
5687 | 31.373
5688 | 31.372
5689 | 31.371
5690 | 31.37
5691 | 31.369
5692 | 31.368
5693 | 31.366
5694 | 31.363
5695 | 31.362
5696 | 31.361
5697 | 31.36
5698 | 31.36
5699 | 31.357
5700 | 31.354
5701 | 31.354
5702 | 31.354
5703 | 31.352
5704 | 31.351
5705 | 31.351
5706 | 31.35
5707 | 31.346
5708 | 31.345
5709 | 31.344
5710 | 31.343
5711 | 31.342
5712 | 31.34
5713 | 31.34
5714 | 31.338
5715 | 31.338
5716 | 31.335
5717 | 31.335
5718 | 31.333
5719 | 31.333
5720 | 31.332
5721 | 31.332
5722 | 31.331
5723 | 31.331
5724 | 31.329
5725 | 31.328
5726 | 31.326
5727 | 31.326
5728 | 31.325
5729 | 31.322
5730 | 31.321
5731 | 31.321
5732 | 31.32
5733 | 31.319
5734 | 31.318
5735 | 31.315
5736 | 31.313
5737 | 31.31
5738 | 31.306
5739 | 31.305
5740 | 31.304
5741 | 31.3
5742 | 31.3
5743 | 31.297
5744 | 31.293
5745 | 31.292
5746 | 31.292
5747 | 31.291
5748 | 31.291
5749 | 31.287
5750 | 31.287
5751 | 31.285
5752 | 31.282
5753 | 31.281
5754 | 31.278
5755 | 31.275
5756 | 31.273
5757 | 31.271
5758 | 31.271
5759 | 31.27
5760 | 31.268
5761 | 31.268
5762 | 31.265
5763 | 31.262
5764 | 31.26
5765 | 31.256
5766 | 31.256
5767 | 31.253
5768 | 31.251
5769 | 31.251
5770 | 31.251
5771 | 31.25
5772 | 31.25
5773 | 31.249
5774 | 31.247
5775 | 31.246
5776 | 31.246
5777 | 31.246
5778 | 31.245
5779 | 31.242
5780 | 31.241
5781 | 31.238
5782 | 31.238
5783 | 31.238
5784 | 31.237
5785 | 31.236
5786 | 31.234
5787 | 31.232
5788 | 31.231
5789 | 31.231
5790 | 31.23
5791 | 31.23
5792 | 31.228
5793 | 31.227
5794 | 31.226
5795 | 31.225
5796 | 31.223
5797 | 31.223
5798 | 31.222
5799 | 31.221
5800 | 31.22
5801 | 31.219
5802 | 31.218
5803 | 31.218
5804 | 31.216
5805 | 31.213
5806 | 31.211
5807 | 31.21
5808 | 31.206
5809 | 31.205
5810 | 31.202
5811 | 31.202
5812 | 31.199
5813 | 31.198
5814 | 31.198
5815 | 31.198
5816 | 31.197
5817 | 31.196
5818 | 31.195
5819 | 31.195
5820 | 31.194
5821 | 31.193
5822 | 31.191
5823 | 31.191
5824 | 31.191
5825 | 31.186
5826 | 31.185
5827 | 31.183
5828 | 31.18
5829 | 31.179
5830 | 31.178
5831 | 31.174
5832 | 31.174
5833 | 31.174
5834 | 31.173
5835 | 31.173
5836 | 31.171
5837 | 31.171
5838 | 31.169
5839 | 31.169
5840 | 31.168
5841 | 31.167
5842 | 31.167
5843 | 31.167
5844 | 31.163
5845 | 31.161
5846 | 31.157
5847 | 31.156
5848 | 31.156
5849 | 31.152
5850 | 31.152
5851 | 31.151
5852 | 31.151
5853 | 31.151
5854 | 31.151
5855 | 31.15
5856 | 31.149
5857 | 31.149
5858 | 31.148
5859 | 31.146
5860 | 31.146
5861 | 31.143
5862 | 31.142
5863 | 31.141
5864 | 31.137
5865 | 31.136
5866 | 31.135
5867 | 31.131
5868 | 31.131
5869 | 31.131
5870 | 31.13
5871 | 31.13
5872 | 31.13
5873 | 31.13
5874 | 31.129
5875 | 31.127
5876 | 31.126
5877 | 31.125
5878 | 31.124
5879 | 31.123
5880 | 31.121
5881 | 31.12
5882 | 31.118
5883 | 31.118
5884 | 31.116
5885 | 31.113
5886 | 31.11
5887 | 31.107
5888 | 31.106
5889 | 31.104
5890 | 31.103
5891 | 31.103
5892 | 31.102
5893 | 31.098
5894 | 31.098
5895 | 31.098
5896 | 31.098
5897 | 31.097
5898 | 31.097
5899 | 31.097
5900 | 31.095
5901 | 31.092
5902 | 31.092
5903 | 31.092
5904 | 31.091
5905 | 31.09
5906 | 31.088
5907 | 31.087
5908 | 31.084
5909 | 31.082
5910 | 31.082
5911 | 31.082
5912 | 31.081
5913 | 31.078
5914 | 31.077
5915 | 31.076
5916 | 31.072
5917 | 31.071
5918 | 31.07
5919 | 31.066
5920 | 31.065
5921 | 31.065
5922 | 31.063
5923 | 31.063
5924 | 31.061
5925 | 31.061
5926 | 31.059
5927 | 31.058
5928 | 31.058
5929 | 31.058
5930 | 31.051
5931 | 31.047
5932 | 31.044
5933 | 31.042
5934 | 31.041
5935 | 31.04
5936 | 31.039
5937 | 31.037
5938 | 31.037
5939 | 31.036
5940 | 31.036
5941 | 31.035
5942 | 31.034
5943 | 31.032
5944 | 31.032
5945 | 31.032
5946 | 31.031
5947 | 31.031
5948 | 31.027
5949 | 31.026
5950 | 31.024
5951 | 31.023
5952 | 31.022
5953 | 31.021
5954 | 31.02
5955 | 31.019
5956 | 31.019
5957 | 31.018
5958 | 31.016
5959 | 31.015
5960 | 31.014
5961 | 31.013
5962 | 31.013
5963 | 31.011
5964 | 31.005
5965 | 31.004
5966 | 31.004
5967 | 30.999
5968 | 30.999
5969 | 30.995
5970 | 30.993
5971 | 30.992
5972 | 30.991
5973 | 30.987
5974 | 30.987
5975 | 30.986
5976 | 30.984
5977 | 30.981
5978 | 30.981
5979 | 30.98
5980 | 30.979
5981 | 30.979
5982 | 30.978
5983 | 30.977
5984 | 30.977
5985 | 30.972
5986 | 30.971
5987 | 30.966
5988 | 30.965
5989 | 30.964
5990 | 30.963
5991 | 30.962
5992 | 30.96
5993 | 30.959
5994 | 30.957
5995 | 30.955
5996 | 30.952
5997 | 30.951
5998 | 30.948
5999 | 30.948
6000 | 30.946
6001 | 30.945
6002 | 30.941
6003 | 30.94
6004 | 30.94
6005 | 30.939
6006 | 30.939
6007 | 30.937
6008 | 30.937
6009 | 30.935
6010 | 30.935
6011 | 30.934
6012 | 30.931
6013 | 30.928
6014 | 30.928
6015 | 30.928
6016 | 30.926
6017 | 30.926
6018 | 30.926
6019 | 30.924
6020 | 30.924
6021 | 30.923
6022 | 30.921
6023 | 30.921
6024 | 30.919
6025 | 30.915
6026 | 30.915
6027 | 30.915
6028 | 30.915
6029 | 30.914
6030 | 30.913
6031 | 30.913
6032 | 30.912
6033 | 30.911
6034 | 30.911
6035 | 30.91
6036 | 30.91
6037 | 30.907
6038 | 30.906
6039 | 30.906
6040 | 30.904
6041 | 30.901
6042 | 30.9
6043 | 30.899
6044 | 30.897
6045 | 30.897
6046 | 30.896
6047 | 30.892
6048 | 30.891
6049 | 30.89
6050 | 30.89
6051 | 30.887
6052 | 30.886
6053 | 30.886
6054 | 30.884
6055 | 30.884
6056 | 30.883
6057 | 30.882
6058 | 30.882
6059 | 30.877
6060 | 30.877
6061 | 30.876
6062 | 30.874
6063 | 30.874
6064 | 30.87
6065 | 30.866
6066 | 30.865
6067 | 30.864
6068 | 30.863
6069 | 30.863
6070 | 30.86
6071 | 30.858
6072 | 30.858
6073 | 30.858
6074 | 30.857
6075 | 30.856
6076 | 30.855
6077 | 30.854
6078 | 30.854
6079 | 30.853
6080 | 30.853
6081 | 30.848
6082 | 30.848
6083 | 30.847
6084 | 30.845
6085 | 30.844
6086 | 30.844
6087 | 30.842
6088 | 30.841
6089 | 30.841
6090 | 30.841
6091 | 30.84
6092 | 30.84
6093 | 30.839
6094 | 30.839
6095 | 30.839
6096 | 30.838
6097 | 30.833
6098 | 30.833
6099 | 30.833
6100 | 30.832
6101 | 30.831
6102 | 30.83
6103 | 30.83
6104 | 30.83
6105 | 30.83
6106 | 30.829
6107 | 30.829
6108 | 30.828
6109 | 30.827
6110 | 30.825
6111 | 30.825
6112 | 30.823
6113 | 30.819
6114 | 30.817
6115 | 30.816
6116 | 30.816
6117 | 30.815
6118 | 30.814
6119 | 30.81
6120 | 30.809
6121 | 30.808
6122 | 30.806
6123 | 30.806
6124 | 30.804
6125 | 30.804
6126 | 30.804
6127 | 30.803
6128 | 30.802
6129 | 30.801
6130 | 30.8
6131 | 30.799
6132 | 30.797
6133 | 30.797
6134 | 30.796
6135 | 30.796
6136 | 30.794
6137 | 30.793
6138 | 30.791
6139 | 30.791
6140 | 30.791
6141 | 30.79
6142 | 30.788
6143 | 30.788
6144 | 30.786
6145 | 30.783
6146 | 30.781
6147 | 30.779
6148 | 30.777
6149 | 30.776
6150 | 30.775
6151 | 30.774
6152 | 30.774
6153 | 30.773
6154 | 30.773
6155 | 30.772
6156 | 30.771
6157 | 30.77
6158 | 30.769
6159 | 30.768
6160 | 30.767
6161 | 30.765
6162 | 30.765
6163 | 30.761
6164 | 30.759
6165 | 30.758
6166 | 30.758
6167 | 30.752
6168 | 30.752
6169 | 30.751
6170 | 30.75
6171 | 30.748
6172 | 30.748
6173 | 30.748
6174 | 30.748
6175 | 30.747
6176 | 30.745
6177 | 30.741
6178 | 30.741
6179 | 30.74
6180 | 30.739
6181 | 30.737
6182 | 30.736
6183 | 30.734
6184 | 30.733
6185 | 30.733
6186 | 30.73
6187 | 30.724
6188 | 30.724
6189 | 30.724
6190 | 30.724
6191 | 30.723
6192 | 30.719
6193 | 30.719
6194 | 30.717
6195 | 30.716
6196 | 30.714
6197 | 30.713
6198 | 30.712
6199 | 30.711
6200 | 30.71
6201 | 30.708
6202 | 30.707
6203 | 30.706
6204 | 30.706
6205 | 30.705
6206 | 30.704
6207 | 30.701
6208 | 30.698
6209 | 30.697
6210 | 30.696
6211 | 30.696
6212 | 30.695
6213 | 30.694
6214 | 30.693
6215 | 30.69
6216 | 30.69
6217 | 30.688
6218 | 30.685
6219 | 30.685
6220 | 30.684
6221 | 30.684
6222 | 30.684
6223 | 30.683
6224 | 30.682
6225 | 30.682
6226 | 30.681
6227 | 30.681
6228 | 30.68
6229 | 30.679
6230 | 30.677
6231 | 30.677
6232 | 30.677
6233 | 30.677
6234 | 30.675
6235 | 30.673
6236 | 30.673
6237 | 30.671
6238 | 30.669
6239 | 30.669
6240 | 30.668
6241 | 30.668
6242 | 30.667
6243 | 30.665
6244 | 30.664
6245 | 30.662
6246 | 30.661
6247 | 30.66
6248 | 30.659
6249 | 30.658
6250 | 30.658
6251 | 30.657
6252 | 30.657
6253 | 30.657
6254 | 30.655
6255 | 30.654
6256 | 30.654
6257 | 30.653
6258 | 30.65
6259 | 30.649
6260 | 30.649
6261 | 30.648
6262 | 30.646
6263 | 30.645
6264 | 30.644
6265 | 30.643
6266 | 30.642
6267 | 30.641
6268 | 30.639
6269 | 30.638
6270 | 30.637
6271 | 30.636
6272 | 30.635
6273 | 30.632
6274 | 30.631
6275 | 30.63
6276 | 30.63
6277 | 30.628
6278 | 30.622
6279 | 30.622
6280 | 30.62
6281 | 30.618
6282 | 30.617
6283 | 30.617
6284 | 30.615
6285 | 30.615
6286 | 30.61
6287 | 30.607
6288 | 30.604
6289 | 30.601
6290 | 30.6
6291 | 30.597
6292 | 30.596
6293 | 30.595
6294 | 30.592
6295 | 30.591
6296 | 30.588
6297 | 30.588
6298 | 30.585
6299 | 30.584
6300 | 30.583
6301 | 30.581
6302 | 30.58
6303 | 30.579
6304 | 30.579
6305 | 30.579
6306 | 30.578
6307 | 30.575
6308 | 30.57
6309 | 30.569
6310 | 30.568
6311 | 30.565
6312 | 30.564
6313 | 30.562
6314 | 30.561
6315 | 30.561
6316 | 30.559
6317 | 30.557
6318 | 30.556
6319 | 30.549
6320 | 30.549
6321 | 30.545
6322 | 30.544
6323 | 30.544
6324 | 30.544
6325 | 30.542
6326 | 30.54
6327 | 30.538
6328 | 30.538
6329 | 30.536
6330 | 30.536
6331 | 30.535
6332 | 30.534
6333 | 30.53
6334 | 30.529
6335 | 30.528
6336 | 30.528
6337 | 30.526
6338 | 30.526
6339 | 30.526
6340 | 30.523
6341 | 30.522
6342 | 30.522
6343 | 30.519
6344 | 30.518
6345 | 30.518
6346 | 30.518
6347 | 30.517
6348 | 30.517
6349 | 30.516
6350 | 30.515
6351 | 30.515
6352 | 30.515
6353 | 30.515
6354 | 30.513
6355 | 30.512
6356 | 30.51
6357 | 30.51
6358 | 30.508
6359 | 30.506
6360 | 30.506
6361 | 30.505
6362 | 30.505
6363 | 30.504
6364 | 30.502
6365 | 30.501
6366 | 30.5
6367 | 30.499
6368 | 30.496
6369 | 30.496
6370 | 30.494
6371 | 30.493
6372 | 30.493
6373 | 30.491
6374 | 30.49
6375 | 30.49
6376 | 30.489
6377 | 30.488
6378 | 30.488
6379 | 30.487
6380 | 30.486
6381 | 30.484
6382 | 30.484
6383 | 30.483
6384 | 30.482
6385 | 30.48
6386 | 30.479
6387 | 30.471
6388 | 30.465
6389 | 30.462
6390 | 30.46
6391 | 30.459
6392 | 30.457
6393 | 30.455
6394 | 30.452
6395 | 30.448
6396 | 30.446
6397 | 30.445
6398 | 30.444
6399 | 30.444
6400 | 30.444
6401 | 30.438
6402 | 30.438
6403 | 30.438
6404 | 30.43
6405 | 30.43
6406 | 30.429
6407 | 30.428
6408 | 30.424
6409 | 30.421
6410 | 30.42
6411 | 30.417
6412 | 30.416
6413 | 30.414
6414 | 30.414
6415 | 30.414
6416 | 30.414
6417 | 30.409
6418 | 30.405
6419 | 30.404
6420 | 30.404
6421 | 30.401
6422 | 30.395
6423 | 30.393
6424 | 30.392
6425 | 30.39
6426 | 30.389
6427 | 30.385
6428 | 30.385
6429 | 30.38
6430 | 30.378
6431 | 30.373
6432 | 30.372
6433 | 30.37
6434 | 30.367
6435 | 30.364
6436 | 30.364
6437 | 30.362
6438 | 30.361
6439 | 30.36
6440 | 30.356
6441 | 30.356
6442 | 30.356
6443 | 30.354
6444 | 30.351
6445 | 30.349
6446 | 30.347
6447 | 30.347
6448 | 30.346
6449 | 30.343
6450 | 30.342
6451 | 30.34
6452 | 30.339
6453 | 30.338
6454 | 30.336
6455 | 30.332
6456 | 30.33
6457 | 30.33
6458 | 30.33
6459 | 30.329
6460 | 30.327
6461 | 30.327
6462 | 30.322
6463 | 30.318
6464 | 30.318
6465 | 30.316
6466 | 30.315
6467 | 30.314
6468 | 30.311
6469 | 30.31
6470 | 30.308
6471 | 30.305
6472 | 30.304
6473 | 30.303
6474 | 30.3
6475 | 30.3
6476 | 30.3
6477 | 30.296
6478 | 30.295
6479 | 30.288
6480 | 30.282
6481 | 30.279
6482 | 30.278
6483 | 30.276
6484 | 30.269
6485 | 30.26
6486 | 30.259
6487 | 30.259
6488 | 30.258
6489 | 30.254
6490 | 30.253
6491 | 30.252
6492 | 30.252
6493 | 30.248
6494 | 30.248
6495 | 30.243
6496 | 30.243
6497 | 30.243
6498 | 30.24
6499 | 30.24
6500 | 30.238
6501 | 30.238
6502 | 30.237
6503 | 30.237
6504 | 30.236
6505 | 30.236
6506 | 30.234
6507 | 30.234
6508 | 30.234
6509 | 30.229
6510 | 30.229
6511 | 30.229
6512 | 30.227
6513 | 30.226
6514 | 30.226
6515 | 30.223
6516 | 30.222
6517 | 30.221
6518 | 30.22
6519 | 30.218
6520 | 30.217
6521 | 30.217
6522 | 30.217
6523 | 30.213
6524 | 30.21
6525 | 30.208
6526 | 30.207
6527 | 30.207
6528 | 30.207
6529 | 30.206
6530 | 30.202
6531 | 30.199
6532 | 30.198
6533 | 30.198
6534 | 30.197
6535 | 30.197
6536 | 30.193
6537 | 30.193
6538 | 30.191
6539 | 30.19
6540 | 30.187
6541 | 30.181
6542 | 30.179
6543 | 30.177
6544 | 30.177
6545 | 30.172
6546 | 30.17
6547 | 30.169
6548 | 30.169
6549 | 30.167
6550 | 30.162
6551 | 30.16
6552 | 30.16
6553 | 30.159
6554 | 30.158
6555 | 30.158
6556 | 30.157
6557 | 30.153
6558 | 30.15
6559 | 30.145
6560 | 30.145
6561 | 30.143
6562 | 30.143
6563 | 30.142
6564 | 30.141
6565 | 30.139
6566 | 30.138
6567 | 30.137
6568 | 30.136
6569 | 30.134
6570 | 30.133
6571 | 30.133
6572 | 30.133
6573 | 30.133
6574 | 30.131
6575 | 30.129
6576 | 30.127
6577 | 30.125
6578 | 30.125
6579 | 30.123
6580 | 30.121
6581 | 30.119
6582 | 30.117
6583 | 30.116
6584 | 30.114
6585 | 30.112
6586 | 30.108
6587 | 30.108
6588 | 30.106
6589 | 30.105
6590 | 30.104
6591 | 30.103
6592 | 30.101
6593 | 30.1
6594 | 30.094
6595 | 30.093
6596 | 30.092
6597 | 30.092
6598 | 30.09
6599 | 30.088
6600 | 30.088
6601 | 30.085
6602 | 30.084
6603 | 30.083
6604 | 30.083
6605 | 30.081
6606 | 30.079
6607 | 30.078
6608 | 30.077
6609 | 30.075
6610 | 30.074
6611 | 30.072
6612 | 30.068
6613 | 30.068
6614 | 30.065
6615 | 30.06
6616 | 30.056
6617 | 30.053
6618 | 30.05
6619 | 30.049
6620 | 30.047
6621 | 30.047
6622 | 30.044
6623 | 30.043
6624 | 30.04
6625 | 30.04
6626 | 30.035
6627 | 30.032
6628 | 30.032
6629 | 30.03
6630 | 30.029
6631 | 30.027
6632 | 30.026
6633 | 30.025
6634 | 30.024
6635 | 30.019
6636 | 30.019
6637 | 30.016
6638 | 30.013
6639 | 30.01
6640 | 30.008
6641 | 30.008
6642 | 30.007
6643 | 30.007
6644 | 30.007
6645 | 30.001
6646 | 29.999
6647 | 29.997
6648 | 29.994
6649 | 29.993
6650 | 29.991
6651 | 29.987
6652 | 29.987
6653 | 29.986
6654 | 29.984
6655 | 29.983
6656 | 29.982
6657 | 29.97
6658 | 29.967
6659 | 29.962
6660 | 29.957
6661 | 29.956
6662 | 29.954
6663 | 29.951
6664 | 29.949
6665 | 29.941
6666 | 29.94
6667 | 29.94
6668 | 29.937
6669 | 29.935
6670 | 29.935
6671 | 29.934
6672 | 29.934
6673 | 29.933
6674 | 29.933
6675 | 29.932
6676 | 29.932
6677 | 29.931
6678 | 29.93
6679 | 29.93
6680 | 29.929
6681 | 29.929
6682 | 29.928
6683 | 29.916
6684 | 29.916
6685 | 29.912
6686 | 29.907
6687 | 29.906
6688 | 29.905
6689 | 29.905
6690 | 29.905
6691 | 29.902
6692 | 29.901
6693 | 29.897
6694 | 29.891
6695 | 29.891
6696 | 29.891
6697 | 29.89
6698 | 29.888
6699 | 29.882
6700 | 29.881
6701 | 29.881
6702 | 29.88
6703 | 29.877
6704 | 29.874
6705 | 29.87
6706 | 29.868
6707 | 29.864
6708 | 29.86
6709 | 29.859
6710 | 29.857
6711 | 29.857
6712 | 29.849
6713 | 29.847
6714 | 29.847
6715 | 29.845
6716 | 29.844
6717 | 29.843
6718 | 29.841
6719 | 29.84
6720 | 29.839
6721 | 29.839
6722 | 29.834
6723 | 29.825
6724 | 29.825
6725 | 29.823
6726 | 29.819
6727 | 29.816
6728 | 29.81
6729 | 29.809
6730 | 29.808
6731 | 29.805
6732 | 29.805
6733 | 29.804
6734 | 29.804
6735 | 29.8
6736 | 29.799
6737 | 29.796
6738 | 29.79
6739 | 29.787
6740 | 29.786
6741 | 29.784
6742 | 29.783
6743 | 29.782
6744 | 29.78
6745 | 29.776
6746 | 29.776
6747 | 29.776
6748 | 29.772
6749 | 29.77
6750 | 29.77
6751 | 29.769
6752 | 29.768
6753 | 29.768
6754 | 29.758
6755 | 29.755
6756 | 29.754
6757 | 29.754
6758 | 29.753
6759 | 29.752
6760 | 29.752
6761 | 29.752
6762 | 29.752
6763 | 29.751
6764 | 29.75
6765 | 29.749
6766 | 29.748
6767 | 29.746
6768 | 29.744
6769 | 29.743
6770 | 29.743
6771 | 29.742
6772 | 29.738
6773 | 29.737
6774 | 29.736
6775 | 29.735
6776 | 29.733
6777 | 29.733
6778 | 29.731
6779 | 29.725
6780 | 29.725
6781 | 29.724
6782 | 29.722
6783 | 29.719
6784 | 29.714
6785 | 29.714
6786 | 29.712
6787 | 29.71
6788 | 29.706
6789 | 29.705
6790 | 29.702
6791 | 29.701
6792 | 29.699
6793 | 29.699
6794 | 29.698
6795 | 29.696
6796 | 29.694
6797 | 29.689
6798 | 29.687
6799 | 29.687
6800 | 29.687
6801 | 29.686
6802 | 29.685
6803 | 29.684
6804 | 29.68
6805 | 29.68
6806 | 29.677
6807 | 29.67
6808 | 29.667
6809 | 29.665
6810 | 29.665
6811 | 29.659
6812 | 29.659
6813 | 29.656
6814 | 29.631
6815 | 29.631
6816 | 29.63
6817 | 29.629
6818 | 29.629
6819 | 29.627
6820 | 29.625
6821 | 29.622
6822 | 29.622
6823 | 29.617
6824 | 29.615
6825 | 29.612
6826 | 29.605
6827 | 29.601
6828 | 29.599
6829 | 29.598
6830 | 29.598
6831 | 29.593
6832 | 29.592
6833 | 29.591
6834 | 29.59
6835 | 29.59
6836 | 29.583
6837 | 29.582
6838 | 29.581
6839 | 29.578
6840 | 29.576
6841 | 29.573
6842 | 29.572
6843 | 29.566
6844 | 29.566
6845 | 29.557
6846 | 29.556
6847 | 29.553
6848 | 29.552
6849 | 29.551
6850 | 29.549
6851 | 29.547
6852 | 29.547
6853 | 29.545
6854 | 29.544
6855 | 29.542
6856 | 29.54
6857 | 29.537
6858 | 29.534
6859 | 29.534
6860 | 29.533
6861 | 29.53
6862 | 29.53
6863 | 29.53
6864 | 29.529
6865 | 29.528
6866 | 29.528
6867 | 29.527
6868 | 29.521
6869 | 29.519
6870 | 29.519
6871 | 29.519
6872 | 29.518
6873 | 29.515
6874 | 29.513
6875 | 29.512
6876 | 29.509
6877 | 29.509
6878 | 29.508
6879 | 29.506
6880 | 29.5
6881 | 29.489
6882 | 29.488
6883 | 29.487
6884 | 29.485
6885 | 29.481
6886 | 29.478
6887 | 29.476
6888 | 29.475
6889 | 29.474
6890 | 29.471
6891 | 29.468
6892 | 29.468
6893 | 29.466
6894 | 29.465
6895 | 29.465
6896 | 29.463
6897 | 29.463
6898 | 29.462
6899 | 29.46
6900 | 29.46
6901 | 29.459
6902 | 29.459
6903 | 29.454
6904 | 29.445
6905 | 29.442
6906 | 29.437
6907 | 29.435
6908 | 29.435
6909 | 29.426
6910 | 29.425
6911 | 29.421
6912 | 29.421
6913 | 29.419
6914 | 29.418
6915 | 29.415
6916 | 29.409
6917 | 29.408
6918 | 29.408
6919 | 29.406
6920 | 29.404
6921 | 29.404
6922 | 29.403
6923 | 29.401
6924 | 29.395
6925 | 29.394
6926 | 29.393
6927 | 29.39
6928 | 29.389
6929 | 29.387
6930 | 29.381
6931 | 29.38
6932 | 29.38
6933 | 29.379
6934 | 29.379
6935 | 29.377
6936 | 29.376
6937 | 29.372
6938 | 29.371
6939 | 29.367
6940 | 29.366
6941 | 29.363
6942 | 29.363
6943 | 29.361
6944 | 29.359
6945 | 29.349
6946 | 29.345
6947 | 29.344
6948 | 29.341
6949 | 29.339
6950 | 29.339
6951 | 29.338
6952 | 29.331
6953 | 29.32
6954 | 29.319
6955 | 29.319
6956 | 29.319
6957 | 29.317
6958 | 29.314
6959 | 29.31
6960 | 29.309
6961 | 29.305
6962 | 29.303
6963 | 29.302
6964 | 29.298
6965 | 29.297
6966 | 29.295
6967 | 29.291
6968 | 29.29
6969 | 29.287
6970 | 29.286
6971 | 29.277
6972 | 29.276
6973 | 29.276
6974 | 29.272
6975 | 29.272
6976 | 29.268
6977 | 29.267
6978 | 29.264
6979 | 29.263
6980 | 29.261
6981 | 29.261
6982 | 29.256
6983 | 29.256
6984 | 29.255
6985 | 29.253
6986 | 29.252
6987 | 29.248
6988 | 29.248
6989 | 29.247
6990 | 29.246
6991 | 29.246
6992 | 29.246
6993 | 29.241
6994 | 29.24
6995 | 29.238
6996 | 29.235
6997 | 29.229
6998 | 29.229
6999 | 29.229
7000 | 29.228
7001 | 29.226
7002 | 29.223
7003 | 29.222
7004 | 29.215
7005 | 29.207
7006 | 29.206
7007 | 29.199
7008 | 29.198
7009 | 29.194
7010 | 29.191
7011 | 29.191
7012 | 29.19
7013 | 29.185
7014 | 29.18
7015 | 29.174
7016 | 29.167
7017 | 29.165
7018 | 29.163
7019 | 29.161
7020 | 29.16
7021 | 29.16
7022 | 29.158
7023 | 29.158
7024 | 29.154
7025 | 29.152
7026 | 29.147
7027 | 29.141
7028 | 29.137
7029 | 29.136
7030 | 29.135
7031 | 29.135
7032 | 29.13
7033 | 29.127
7034 | 29.126
7035 | 29.117
7036 | 29.111
7037 | 29.109
7038 | 29.105
7039 | 29.103
7040 | 29.1
7041 | 29.097
7042 | 29.094
7043 | 29.092
7044 | 29.081
7045 | 29.081
7046 | 29.08
7047 | 29.078
7048 | 29.076
7049 | 29.069
7050 | 29.066
7051 | 29.066
7052 | 29.066
7053 | 29.065
7054 | 29.06
7055 | 29.06
7056 | 29.056
7057 | 29.056
7058 | 29.055
7059 | 29.055
7060 | 29.054
7061 | 29.05
7062 | 29.049
7063 | 29.048
7064 | 29.046
7065 | 29.046
7066 | 29.046
7067 | 29.046
7068 | 29.044
7069 | 29.038
7070 | 29.034
7071 | 29.032
7072 | 29.03
7073 | 29.027
7074 | 29.026
7075 | 29.018
7076 | 29.01
7077 | 29.007
7078 | 29.005
7079 | 29.004
7080 | 29.001
7081 | 29.001
7082 | 28.998
7083 | 28.997
7084 | 28.996
7085 | 28.995
7086 | 28.992
7087 | 28.987
7088 | 28.987
7089 | 28.986
7090 | 28.984
7091 | 28.983
7092 | 28.982
7093 | 28.981
7094 | 28.979
7095 | 28.978
7096 | 28.978
7097 | 28.977
7098 | 28.977
7099 | 28.975
7100 | 28.961
7101 | 28.959
7102 | 28.949
7103 | 28.947
7104 | 28.943
7105 | 28.941
7106 | 28.937
7107 | 28.933
7108 | 28.932
7109 | 28.929
7110 | 28.928
7111 | 28.925
7112 | 28.924
7113 | 28.923
7114 | 28.918
7115 | 28.915
7116 | 28.914
7117 | 28.909
7118 | 28.908
7119 | 28.906
7120 | 28.904
7121 | 28.899
7122 | 28.896
7123 | 28.895
7124 | 28.893
7125 | 28.89
7126 | 28.887
7127 | 28.882
7128 | 28.879
7129 | 28.874
7130 | 28.87
7131 | 28.869
7132 | 28.866
7133 | 28.859
7134 | 28.853
7135 | 28.852
7136 | 28.851
7137 | 28.846
7138 | 28.846
7139 | 28.844
7140 | 28.84
7141 | 28.84
7142 | 28.839
7143 | 28.835
7144 | 28.826
7145 | 28.826
7146 | 28.824
7147 | 28.821
7148 | 28.82
7149 | 28.817
7150 | 28.816
7151 | 28.816
7152 | 28.815
7153 | 28.814
7154 | 28.812
7155 | 28.81
7156 | 28.806
7157 | 28.805
7158 | 28.803
7159 | 28.802
7160 | 28.802
7161 | 28.798
7162 | 28.797
7163 | 28.797
7164 | 28.79
7165 | 28.789
7166 | 28.787
7167 | 28.784
7168 | 28.783
7169 | 28.781
7170 | 28.776
7171 | 28.775
7172 | 28.772
7173 | 28.772
7174 | 28.771
7175 | 28.769
7176 | 28.765
7177 | 28.764
7178 | 28.763
7179 | 28.762
7180 | 28.761
7181 | 28.75
7182 | 28.749
7183 | 28.744
7184 | 28.741
7185 | 28.74
7186 | 28.738
7187 | 28.736
7188 | 28.734
7189 | 28.727
7190 | 28.723
7191 | 28.723
7192 | 28.723
7193 | 28.723
7194 | 28.719
7195 | 28.714
7196 | 28.713
7197 | 28.711
7198 | 28.704
7199 | 28.703
7200 | 28.702
7201 | 28.702
7202 | 28.699
7203 | 28.691
7204 | 28.69
7205 | 28.686
7206 | 28.685
7207 | 28.682
7208 | 28.68
7209 | 28.68
7210 | 28.676
7211 | 28.673
7212 | 28.671
7213 | 28.67
7214 | 28.668
7215 | 28.668
7216 | 28.668
7217 | 28.664
7218 | 28.658
7219 | 28.657
7220 | 28.645
7221 | 28.644
7222 | 28.64
7223 | 28.64
7224 | 28.638
7225 | 28.634
7226 | 28.627
7227 | 28.625
7228 | 28.624
7229 | 28.624
7230 | 28.616
7231 | 28.614
7232 | 28.61
7233 | 28.602
7234 | 28.602
7235 | 28.601
7236 | 28.601
7237 | 28.597
7238 | 28.597
7239 | 28.597
7240 | 28.596
7241 | 28.595
7242 | 28.592
7243 | 28.59
7244 | 28.585
7245 | 28.583
7246 | 28.576
7247 | 28.575
7248 | 28.573
7249 | 28.572
7250 | 28.57
7251 | 28.57
7252 | 28.57
7253 | 28.559
7254 | 28.557
7255 | 28.557
7256 | 28.555
7257 | 28.554
7258 | 28.551
7259 | 28.547
7260 | 28.546
7261 | 28.546
7262 | 28.543
7263 | 28.543
7264 | 28.539
7265 | 28.534
7266 | 28.533
7267 | 28.529
7268 | 28.525
7269 | 28.522
7270 | 28.52
7271 | 28.517
7272 | 28.512
7273 | 28.511
7274 | 28.509
7275 | 28.507
7276 | 28.506
7277 | 28.504
7278 | 28.498
7279 | 28.498
7280 | 28.495
7281 | 28.494
7282 | 28.491
7283 | 28.489
7284 | 28.487
7285 | 28.486
7286 | 28.483
7287 | 28.48
7288 | 28.477
7289 | 28.471
7290 | 28.47
7291 | 28.469
7292 | 28.469
7293 | 28.468
7294 | 28.461
7295 | 28.461
7296 | 28.454
7297 | 28.453
7298 | 28.45
7299 | 28.445
7300 | 28.445
7301 | 28.44
7302 | 28.435
7303 | 28.42
7304 | 28.412
7305 | 28.411
7306 | 28.393
7307 | 28.391
7308 | 28.389
7309 | 28.389
7310 | 28.386
7311 | 28.382
7312 | 28.38
7313 | 28.379
7314 | 28.376
7315 | 28.373
7316 | 28.372
7317 | 28.37
7318 | 28.369
7319 | 28.367
7320 | 28.363
7321 | 28.363
7322 | 28.361
7323 | 28.348
7324 | 28.348
7325 | 28.345
7326 | 28.343
7327 | 28.341
7328 | 28.34
7329 | 28.34
7330 | 28.338
7331 | 28.338
7332 | 28.335
7333 | 28.334
7334 | 28.327
7335 | 28.325
7336 | 28.321
7337 | 28.32
7338 | 28.313
7339 | 28.312
7340 | 28.309
7341 | 28.307
7342 | 28.305
7343 | 28.303
7344 | 28.3
7345 | 28.297
7346 | 28.295
7347 | 28.295
7348 | 28.294
7349 | 28.294
7350 | 28.293
7351 | 28.292
7352 | 28.284
7353 | 28.281
7354 | 28.279
7355 | 28.279
7356 | 28.275
7357 | 28.269
7358 | 28.267
7359 | 28.262
7360 | 28.261
7361 | 28.259
7362 | 28.258
7363 | 28.254
7364 | 28.248
7365 | 28.248
7366 | 28.247
7367 | 28.239
7368 | 28.238
7369 | 28.234
7370 | 28.227
7371 | 28.226
7372 | 28.225
7373 | 28.225
7374 | 28.222
7375 | 28.216
7376 | 28.214
7377 | 28.214
7378 | 28.213
7379 | 28.213
7380 | 28.213
7381 | 28.212
7382 | 28.21
7383 | 28.21
7384 | 28.197
7385 | 28.193
7386 | 28.193
7387 | 28.192
7388 | 28.191
7389 | 28.188
7390 | 28.187
7391 | 28.185
7392 | 28.179
7393 | 28.176
7394 | 28.175
7395 | 28.171
7396 | 28.164
7397 | 28.16
7398 | 28.16
7399 | 28.16
7400 | 28.158
7401 | 28.157
7402 | 28.155
7403 | 28.151
7404 | 28.147
7405 | 28.144
7406 | 28.143
7407 | 28.141
7408 | 28.134
7409 | 28.121
7410 | 28.116
7411 | 28.114
7412 | 28.113
7413 | 28.111
7414 | 28.109
7415 | 28.106
7416 | 28.102
7417 | 28.102
7418 | 28.102
7419 | 28.1
7420 | 28.098
7421 | 28.097
7422 | 28.093
7423 | 28.089
7424 | 28.085
7425 | 28.078
7426 | 28.075
7427 | 28.072
7428 | 28.07
7429 | 28.068
7430 | 28.062
7431 | 28.052
7432 | 28.051
7433 | 28.042
7434 | 28.037
7435 | 28.037
7436 | 28.036
7437 | 28.035
7438 | 28.031
7439 | 28.03
7440 | 28.014
7441 | 28.008
7442 | 28.007
7443 | 28.005
7444 | 28.002
7445 | 28.002
7446 | 28.001
7447 | 27.998
7448 | 27.984
7449 | 27.981
7450 | 27.979
7451 | 27.977
7452 | 27.962
7453 | 27.943
7454 | 27.943
7455 | 27.94
7456 | 27.939
7457 | 27.937
7458 | 27.933
7459 | 27.927
7460 | 27.927
7461 | 27.924
7462 | 27.921
7463 | 27.915
7464 | 27.913
7465 | 27.913
7466 | 27.912
7467 | 27.909
7468 | 27.907
7469 | 27.887
7470 | 27.884
7471 | 27.883
7472 | 27.883
7473 | 27.882
7474 | 27.88
7475 | 27.876
7476 | 27.872
7477 | 27.872
7478 | 27.866
7479 | 27.863
7480 | 27.861
7481 | 27.861
7482 | 27.861
7483 | 27.86
7484 | 27.859
7485 | 27.855
7486 | 27.854
7487 | 27.851
7488 | 27.85
7489 | 27.843
7490 | 27.842
7491 | 27.842
7492 | 27.842
7493 | 27.836
7494 | 27.835
7495 | 27.834
7496 | 27.833
7497 | 27.821
7498 | 27.821
7499 | 27.817
7500 | 27.814
7501 | 27.811
7502 | 27.811
7503 | 27.809
7504 | 27.799
7505 | 27.799
7506 | 27.799
7507 | 27.797
7508 | 27.796
7509 | 27.792
7510 | 27.783
7511 | 27.782
7512 | 27.779
7513 | 27.778
7514 | 27.778
7515 | 27.776
7516 | 27.773
7517 | 27.773
7518 | 27.768
7519 | 27.765
7520 | 27.76
7521 | 27.755
7522 | 27.755
7523 | 27.753
7524 | 27.753
7525 | 27.748
7526 | 27.747
7527 | 27.744
7528 | 27.743
7529 | 27.732
7530 | 27.731
7531 | 27.729
7532 | 27.728
7533 | 27.727
7534 | 27.719
7535 | 27.718
7536 | 27.716
7537 | 27.715
7538 | 27.707
7539 | 27.707
7540 | 27.707
7541 | 27.705
7542 | 27.702
7543 | 27.7
7544 | 27.698
7545 | 27.679
7546 | 27.675
7547 | 27.673
7548 | 27.659
7549 | 27.653
7550 | 27.652
7551 | 27.645
7552 | 27.642
7553 | 27.635
7554 | 27.634
7555 | 27.63
7556 | 27.623
7557 | 27.616
7558 | 27.615
7559 | 27.614
7560 | 27.602
7561 | 27.6
7562 | 27.596
7563 | 27.591
7564 | 27.59
7565 | 27.582
7566 | 27.58
7567 | 27.577
7568 | 27.575
7569 | 27.574
7570 | 27.571
7571 | 27.571
7572 | 27.569
7573 | 27.567
7574 | 27.565
7575 | 27.563
7576 | 27.558
7577 | 27.552
7578 | 27.55
7579 | 27.534
7580 | 27.532
7581 | 27.532
7582 | 27.521
7583 | 27.511
7584 | 27.507
7585 | 27.505
7586 | 27.501
7587 | 27.5
7588 | 27.498
7589 | 27.495
7590 | 27.488
7591 | 27.487
7592 | 27.483
7593 | 27.477
7594 | 27.471
7595 | 27.469
7596 | 27.469
7597 | 27.469
7598 | 27.466
7599 | 27.46
7600 | 27.456
7601 | 27.454
7602 | 27.446
7603 | 27.44
7604 | 27.43
7605 | 27.428
7606 | 27.425
7607 | 27.425
7608 | 27.424
7609 | 27.419
7610 | 27.419
7611 | 27.416
7612 | 27.415
7613 | 27.415
7614 | 27.413
7615 | 27.412
7616 | 27.407
7617 | 27.404
7618 | 27.4
7619 | 27.396
7620 | 27.393
7621 | 27.391
7622 | 27.387
7623 | 27.387
7624 | 27.385
7625 | 27.382
7626 | 27.38
7627 | 27.379
7628 | 27.376
7629 | 27.375
7630 | 27.368
7631 | 27.366
7632 | 27.361
7633 | 27.359
7634 | 27.354
7635 | 27.35
7636 | 27.343
7637 | 27.34
7638 | 27.339
7639 | 27.333
7640 | 27.329
7641 | 27.328
7642 | 27.325
7643 | 27.319
7644 | 27.31
7645 | 27.308
7646 | 27.307
7647 | 27.304
7648 | 27.299
7649 | 27.299
7650 | 27.296
7651 | 27.296
7652 | 27.292
7653 | 27.29
7654 | 27.289
7655 | 27.283
7656 | 27.266
7657 | 27.264
7658 | 27.263
7659 | 27.254
7660 | 27.251
7661 | 27.25
7662 | 27.248
7663 | 27.243
7664 | 27.229
7665 | 27.227
7666 | 27.224
7667 | 27.222
7668 | 27.222
7669 | 27.219
7670 | 27.216
7671 | 27.204
7672 | 27.202
7673 | 27.201
7674 | 27.2
7675 | 27.194
7676 | 27.194
7677 | 27.191
7678 | 27.187
7679 | 27.178
7680 | 27.175
7681 | 27.175
7682 | 27.164
7683 | 27.164
7684 | 27.158
7685 | 27.153
7686 | 27.148
7687 | 27.145
7688 | 27.137
7689 | 27.132
7690 | 27.127
7691 | 27.126
7692 | 27.123
7693 | 27.118
7694 | 27.114
7695 | 27.114
7696 | 27.114
7697 | 27.11
7698 | 27.108
7699 | 27.1
7700 | 27.097
7701 | 27.096
7702 | 27.095
7703 | 27.084
7704 | 27.084
7705 | 27.075
7706 | 27.073
7707 | 27.07
7708 | 27.068
7709 | 27.068
7710 | 27.067
7711 | 27.065
7712 | 27.06
7713 | 27.04
7714 | 27.038
7715 | 27.034
7716 | 27.032
7717 | 27.031
7718 | 27.023
7719 | 27.022
7720 | 27.018
7721 | 27.015
7722 | 27.008
7723 | 27.007
7724 | 27.005
7725 | 27
7726 | 27
7727 | 27
7728 | 26.999
7729 | 26.993
7730 | 26.99
7731 | 26.989
7732 | 26.976
7733 | 26.965
7734 | 26.953
7735 | 26.949
7736 | 26.947
7737 | 26.943
7738 | 26.939
7739 | 26.939
7740 | 26.934
7741 | 26.931
7742 | 26.929
7743 | 26.925
7744 | 26.925
7745 | 26.92
7746 | 26.918
7747 | 26.916
7748 | 26.912
7749 | 26.902
7750 | 26.901
7751 | 26.897
7752 | 26.893
7753 | 26.89
7754 | 26.89
7755 | 26.882
7756 | 26.875
7757 | 26.869
7758 | 26.863
7759 | 26.863
7760 | 26.86
7761 | 26.855
7762 | 26.853
7763 | 26.852
7764 | 26.85
7765 | 26.849
7766 | 26.847
7767 | 26.846
7768 | 26.846
7769 | 26.846
7770 | 26.845
7771 | 26.839
7772 | 26.833
7773 | 26.829
7774 | 26.829
7775 | 26.828
7776 | 26.824
7777 | 26.823
7778 | 26.822
7779 | 26.821
7780 | 26.81
7781 | 26.808
7782 | 26.807
7783 | 26.803
7784 | 26.799
7785 | 26.796
7786 | 26.793
7787 | 26.78
7788 | 26.779
7789 | 26.77
7790 | 26.755
7791 | 26.749
7792 | 26.74
7793 | 26.737
7794 | 26.734
7795 | 26.733
7796 | 26.732
7797 | 26.725
7798 | 26.722
7799 | 26.72
7800 | 26.712
7801 | 26.71
7802 | 26.71
7803 | 26.702
7804 | 26.692
7805 | 26.69
7806 | 26.686
7807 | 26.684
7808 | 26.677
7809 | 26.663
7810 | 26.662
7811 | 26.662
7812 | 26.653
7813 | 26.653
7814 | 26.648
7815 | 26.648
7816 | 26.64
7817 | 26.64
7818 | 26.638
7819 | 26.626
7820 | 26.619
7821 | 26.617
7822 | 26.614
7823 | 26.612
7824 | 26.61
7825 | 26.606
7826 | 26.606
7827 | 26.601
7828 | 26.598
7829 | 26.597
7830 | 26.589
7831 | 26.588
7832 | 26.584
7833 | 26.582
7834 | 26.575
7835 | 26.574
7836 | 26.573
7837 | 26.572
7838 | 26.564
7839 | 26.563
7840 | 26.553
7841 | 26.553
7842 | 26.552
7843 | 26.548
7844 | 26.547
7845 | 26.544
7846 | 26.541
7847 | 26.54
7848 | 26.522
7849 | 26.52
7850 | 26.508
7851 | 26.505
7852 | 26.501
7853 | 26.501
7854 | 26.499
7855 | 26.484
7856 | 26.482
7857 | 26.474
7858 | 26.47
7859 | 26.465
7860 | 26.461
7861 | 26.459
7862 | 26.456
7863 | 26.452
7864 | 26.448
7865 | 26.448
7866 | 26.446
7867 | 26.437
7868 | 26.426
7869 | 26.426
7870 | 26.421
7871 | 26.419
7872 | 26.418
7873 | 26.415
7874 | 26.408
7875 | 26.407
7876 | 26.397
7877 | 26.395
7878 | 26.395
7879 | 26.393
7880 | 26.384
7881 | 26.378
7882 | 26.376
7883 | 26.372
7884 | 26.367
7885 | 26.361
7886 | 26.359
7887 | 26.35
7888 | 26.35
7889 | 26.346
7890 | 26.341
7891 | 26.34
7892 | 26.337
7893 | 26.335
7894 | 26.331
7895 | 26.327
7896 | 26.324
7897 | 26.314
7898 | 26.313
7899 | 26.313
7900 | 26.308
7901 | 26.303
7902 | 26.291
7903 | 26.29
7904 | 26.283
7905 | 26.281
7906 | 26.279
7907 | 26.279
7908 | 26.276
7909 | 26.274
7910 | 26.267
7911 | 26.26
7912 | 26.255
7913 | 26.253
7914 | 26.252
7915 | 26.24
7916 | 26.24
7917 | 26.233
7918 | 26.23
7919 | 26.225
7920 | 26.219
7921 | 26.218
7922 | 26.21
7923 | 26.21
7924 | 26.207
7925 | 26.202
7926 | 26.198
7927 | 26.191
7928 | 26.191
7929 | 26.175
7930 | 26.169
7931 | 26.165
7932 | 26.164
7933 | 26.151
7934 | 26.15
7935 | 26.147
7936 | 26.147
7937 | 26.143
7938 | 26.13
7939 | 26.128
7940 | 26.128
7941 | 26.124
7942 | 26.12
7943 | 26.118
7944 | 26.114
7945 | 26.113
7946 | 26.1
7947 | 26.097
7948 | 26.096
7949 | 26.091
7950 | 26.074
7951 | 26.07
7952 | 26.069
7953 | 26.065
7954 | 26.061
7955 | 26.055
7956 | 26.029
7957 | 26.023
7958 | 26.019
7959 | 26.015
7960 | 26.013
7961 | 26.011
7962 | 26.007
7963 | 26.005
7964 | 26.004
7965 | 26.003
7966 | 26.003
7967 | 25.997
7968 | 25.987
7969 | 25.974
7970 | 25.972
7971 | 25.97
7972 | 25.959
7973 | 25.958
7974 | 25.953
7975 | 25.953
7976 | 25.948
7977 | 25.947
7978 | 25.945
7979 | 25.939
7980 | 25.937
7981 | 25.933
7982 | 25.918
7983 | 25.91
7984 | 25.908
7985 | 25.903
7986 | 25.9
7987 | 25.897
7988 | 25.897
7989 | 25.893
7990 | 25.884
7991 | 25.88
7992 | 25.878
7993 | 25.876
7994 | 25.87
7995 | 25.857
7996 | 25.856
7997 | 25.84
7998 | 25.839
7999 | 25.838
8000 | 25.827
8001 | 25.826
8002 | 25.82
8003 | 25.819
8004 | 25.818
8005 | 25.806
8006 | 25.806
8007 | 25.805
8008 | 25.797
8009 | 25.78
8010 | 25.78
8011 | 25.779
8012 | 25.756
8013 | 25.75
8014 | 25.747
8015 | 25.746
8016 | 25.724
8017 | 25.723
8018 | 25.721
8019 | 25.713
8020 | 25.707
8021 | 25.697
8022 | 25.694
8023 | 25.692
8024 | 25.683
8025 | 25.679
8026 | 25.667
8027 | 25.663
8028 | 25.659
8029 | 25.656
8030 | 25.651
8031 | 25.65
8032 | 25.641
8033 | 25.64
8034 | 25.637
8035 | 25.635
8036 | 25.63
8037 | 25.63
8038 | 25.628
8039 | 25.616
8040 | 25.614
8041 | 25.604
8042 | 25.598
8043 | 25.596
8044 | 25.591
8045 | 25.586
8046 | 25.585
8047 | 25.585
8048 | 25.584
8049 | 25.583
8050 | 25.58
8051 | 25.576
8052 | 25.571
8053 | 25.57
8054 | 25.569
8055 | 25.569
8056 | 25.568
8057 | 25.568
8058 | 25.564
8059 | 25.559
8060 | 25.549
8061 | 25.547
8062 | 25.546
8063 | 25.545
8064 | 25.541
8065 | 25.534
8066 | 25.533
8067 | 25.531
8068 | 25.528
8069 | 25.521
8070 | 25.508
8071 | 25.499
8072 | 25.496
8073 | 25.494
8074 | 25.493
8075 | 25.492
8076 | 25.489
8077 | 25.489
8078 | 25.481
8079 | 25.46
8080 | 25.46
8081 | 25.457
8082 | 25.456
8083 | 25.455
8084 | 25.448
8085 | 25.447
8086 | 25.435
8087 | 25.433
8088 | 25.43
8089 | 25.427
8090 | 25.424
8091 | 25.411
8092 | 25.408
8093 | 25.403
8094 | 25.399
8095 | 25.395
8096 | 25.394
8097 | 25.379
8098 | 25.377
8099 | 25.374
8100 | 25.374
8101 | 25.371
8102 | 25.369
8103 | 25.368
8104 | 25.367
8105 | 25.365
8106 | 25.358
8107 | 25.358
8108 | 25.341
8109 | 25.336
8110 | 25.333
8111 | 25.332
8112 | 25.33
8113 | 25.33
8114 | 25.329
8115 | 25.326
8116 | 25.323
8117 | 25.313
8118 | 25.312
8119 | 25.311
8120 | 25.31
8121 | 25.306
8122 | 25.303
8123 | 25.286
8124 | 25.286
8125 | 25.279
8126 | 25.273
8127 | 25.268
8128 | 25.267
8129 | 25.264
8130 | 25.259
8131 | 25.245
8132 | 25.243
8133 | 25.243
8134 | 25.243
8135 | 25.241
8136 | 25.24
8137 | 25.236
8138 | 25.236
8139 | 25.23
8140 | 25.227
8141 | 25.224
8142 | 25.221
8143 | 25.221
8144 | 25.219
8145 | 25.216
8146 | 25.213
8147 | 25.209
8148 | 25.204
8149 | 25.191
8150 | 25.186
8151 | 25.184
8152 | 25.172
8153 | 25.167
8154 | 25.153
8155 | 25.151
8156 | 25.148
8157 | 25.143
8158 | 25.143
8159 | 25.14
8160 | 25.131
8161 | 25.131
8162 | 25.131
8163 | 25.124
8164 | 25.116
8165 | 25.107
8166 | 25.106
8167 | 25.1
8168 | 25.099
8169 | 25.099
8170 | 25.095
8171 | 25.089
8172 | 25.072
8173 | 25.065
8174 | 25.061
8175 | 25.058
8176 | 25.054
8177 | 25.051
8178 | 25.043
8179 | 25.04
8180 | 25.036
8181 | 25.035
8182 | 25.034
8183 | 25.033
8184 | 25.028
8185 | 25.027
8186 | 25.019
8187 | 25.014
8188 | 25.007
8189 | 25.003
8190 | 24.999
8191 | 24.999
8192 | 24.999
8193 | 24.994
8194 | 24.986
8195 | 24.985
8196 | 24.982
8197 | 24.982
8198 | 24.974
8199 | 24.973
8200 | 24.964
8201 | 24.963
8202 | 24.957
8203 | 24.955
8204 | 24.948
8205 | 24.939
8206 | 24.937
8207 | 24.935
8208 | 24.935
8209 | 24.93
8210 | 24.927
8211 | 24.925
8212 | 24.923
8213 | 24.915
8214 | 24.902
8215 | 24.902
8216 | 24.898
8217 | 24.898
8218 | 24.892
8219 | 24.891
8220 | 24.884
8221 | 24.88
8222 | 24.877
8223 | 24.86
8224 | 24.854
8225 | 24.85
8226 | 24.843
8227 | 24.833
8228 | 24.82
8229 | 24.819
8230 | 24.818
8231 | 24.817
8232 | 24.815
8233 | 24.807
8234 | 24.804
8235 | 24.803
8236 | 24.801
8237 | 24.797
8238 | 24.791
8239 | 24.786
8240 | 24.781
8241 | 24.774
8242 | 24.769
8243 | 24.762
8244 | 24.76
8245 | 24.759
8246 | 24.759
8247 | 24.758
8248 | 24.758
8249 | 24.757
8250 | 24.755
8251 | 24.75
8252 | 24.748
8253 | 24.748
8254 | 24.743
8255 | 24.74
8256 | 24.739
8257 | 24.736
8258 | 24.735
8259 | 24.721
8260 | 24.719
8261 | 24.712
8262 | 24.709
8263 | 24.705
8264 | 24.705
8265 | 24.693
8266 | 24.691
8267 | 24.69
8268 | 24.688
8269 | 24.681
8270 | 24.681
8271 | 24.666
8272 | 24.664
8273 | 24.657
8274 | 24.642
8275 | 24.637
8276 | 24.634
8277 | 24.623
8278 | 24.621
8279 | 24.618
8280 | 24.617
8281 | 24.604
8282 | 24.603
8283 | 24.602
8284 | 24.598
8285 | 24.593
8286 | 24.591
8287 | 24.59
8288 | 24.59
8289 | 24.588
8290 | 24.579
8291 | 24.578
8292 | 24.576
8293 | 24.573
8294 | 24.573
8295 | 24.571
8296 | 24.569
8297 | 24.568
8298 | 24.56
8299 | 24.556
8300 | 24.554
8301 | 24.549
8302 | 24.543
8303 | 24.537
8304 | 24.529
8305 | 24.523
8306 | 24.517
8307 | 24.512
8308 | 24.511
8309 | 24.511
8310 | 24.51
8311 | 24.508
8312 | 24.507
8313 | 24.503
8314 | 24.499
8315 | 24.495
8316 | 24.494
8317 | 24.493
8318 | 24.491
8319 | 24.487
8320 | 24.477
8321 | 24.476
8322 | 24.467
8323 | 24.46
8324 | 24.451
8325 | 24.442
8326 | 24.441
8327 | 24.439
8328 | 24.433
8329 | 24.431
8330 | 24.43
8331 | 24.427
8332 | 24.426
8333 | 24.419
8334 | 24.406
8335 | 24.405
8336 | 24.397
8337 | 24.394
8338 | 24.391
8339 | 24.373
8340 | 24.368
8341 | 24.362
8342 | 24.362
8343 | 24.36
8344 | 24.359
8345 | 24.356
8346 | 24.353
8347 | 24.345
8348 | 24.344
8349 | 24.341
8350 | 24.322
8351 | 24.318
8352 | 24.316
8353 | 24.314
8354 | 24.312
8355 | 24.308
8356 | 24.304
8357 | 24.304
8358 | 24.301
8359 | 24.296
8360 | 24.276
8361 | 24.254
8362 | 24.252
8363 | 24.251
8364 | 24.248
8365 | 24.247
8366 | 24.241
8367 | 24.241
8368 | 24.241
8369 | 24.238
8370 | 24.236
8371 | 24.233
8372 | 24.229
8373 | 24.229
8374 | 24.229
8375 | 24.227
8376 | 24.216
8377 | 24.213
8378 | 24.203
8379 | 24.198
8380 | 24.197
8381 | 24.187
8382 | 24.187
8383 | 24.186
8384 | 24.185
8385 | 24.181
8386 | 24.181
8387 | 24.175
8388 | 24.171
8389 | 24.155
8390 | 24.154
8391 | 24.153
8392 | 24.14
8393 | 24.139
8394 | 24.132
8395 | 24.123
8396 | 24.122
8397 | 24.12
8398 | 24.116
8399 | 24.109
8400 | 24.105
8401 | 24.098
8402 | 24.086
8403 | 24.085
8404 | 24.08
8405 | 24.079
8406 | 24.073
8407 | 24.072
8408 | 24.068
8409 | 24.062
8410 | 24.062
8411 | 24.06
8412 | 24.059
8413 | 24.054
8414 | 24.051
8415 | 24.051
8416 | 24.05
8417 | 24.046
8418 | 24.044
8419 | 24.041
8420 | 24.038
8421 | 24.036
8422 | 24.03
8423 | 24.029
8424 | 24.021
8425 | 24.013
8426 | 24.012
8427 | 24.01
8428 | 24.01
8429 | 24.007
8430 | 24.006
8431 | 23.998
8432 | 23.996
8433 | 23.99
8434 | 23.99
8435 | 23.985
8436 | 23.978
8437 | 23.976
8438 | 23.972
8439 | 23.964
8440 | 23.954
8441 | 23.951
8442 | 23.943
8443 | 23.928
8444 | 23.921
8445 | 23.918
8446 | 23.913
8447 | 23.906
8448 | 23.905
8449 | 23.904
8450 | 23.894
8451 | 23.89
8452 | 23.89
8453 | 23.87
8454 | 23.868
8455 | 23.867
8456 | 23.866
8457 | 23.855
8458 | 23.849
8459 | 23.844
8460 | 23.839
8461 | 23.836
8462 | 23.83
8463 | 23.828
8464 | 23.825
8465 | 23.82
8466 | 23.818
8467 | 23.813
8468 | 23.812
8469 | 23.812
8470 | 23.805
8471 | 23.798
8472 | 23.798
8473 | 23.796
8474 | 23.79
8475 | 23.787
8476 | 23.784
8477 | 23.779
8478 | 23.777
8479 | 23.775
8480 | 23.772
8481 | 23.771
8482 | 23.767
8483 | 23.766
8484 | 23.755
8485 | 23.754
8486 | 23.754
8487 | 23.747
8488 | 23.744
8489 | 23.743
8490 | 23.741
8491 | 23.727
8492 | 23.723
8493 | 23.703
8494 | 23.695
8495 | 23.689
8496 | 23.688
8497 | 23.686
8498 | 23.681
8499 | 23.676
8500 | 23.674
8501 | 23.671
8502 | 23.669
8503 | 23.66
8504 | 23.654
8505 | 23.645
8506 | 23.643
8507 | 23.643
8508 | 23.636
8509 | 23.633
8510 | 23.633
8511 | 23.631
8512 | 23.626
8513 | 23.626
8514 | 23.619
8515 | 23.609
8516 | 23.608
8517 | 23.604
8518 | 23.603
8519 | 23.602
8520 | 23.6
8521 | 23.595
8522 | 23.588
8523 | 23.575
8524 | 23.574
8525 | 23.569
8526 | 23.567
8527 | 23.566
8528 | 23.559
8529 | 23.553
8530 | 23.544
8531 | 23.539
8532 | 23.534
8533 | 23.525
8534 | 23.525
8535 | 23.521
8536 | 23.521
8537 | 23.521
8538 | 23.512
8539 | 23.51
8540 | 23.508
8541 | 23.506
8542 | 23.5
8543 | 23.497
8544 | 23.492
8545 | 23.489
8546 | 23.487
8547 | 23.486
8548 | 23.486
8549 | 23.483
8550 | 23.473
8551 | 23.473
8552 | 23.472
8553 | 23.469
8554 | 23.469
8555 | 23.466
8556 | 23.466
8557 | 23.466
8558 | 23.465
8559 | 23.464
8560 | 23.448
8561 | 23.446
8562 | 23.443
8563 | 23.44
8564 | 23.437
8565 | 23.432
8566 | 23.432
8567 | 23.432
8568 | 23.432
8569 | 23.43
8570 | 23.425
8571 | 23.423
8572 | 23.422
8573 | 23.421
8574 | 23.42
8575 | 23.417
8576 | 23.416
8577 | 23.411
8578 | 23.403
8579 | 23.403
8580 | 23.401
8581 | 23.39
8582 | 23.389
8583 | 23.388
8584 | 23.387
8585 | 23.384
8586 | 23.382
8587 | 23.38
8588 | 23.366
8589 | 23.366
8590 | 23.36
8591 | 23.358
8592 | 23.349
8593 | 23.33
8594 | 23.328
8595 | 23.326
8596 | 23.324
8597 | 23.321
8598 | 23.319
8599 | 23.318
8600 | 23.318
8601 | 23.317
8602 | 23.311
8603 | 23.305
8604 | 23.302
8605 | 23.292
8606 | 23.288
8607 | 23.285
8608 | 23.282
8609 | 23.281
8610 | 23.28
8611 | 23.271
8612 | 23.265
8613 | 23.253
8614 | 23.247
8615 | 23.242
8616 | 23.241
8617 | 23.24
8618 | 23.239
8619 | 23.237
8620 | 23.227
8621 | 23.225
8622 | 23.222
8623 | 23.219
8624 | 23.21
8625 | 23.206
8626 | 23.202
8627 | 23.199
8628 | 23.197
8629 | 23.193
8630 | 23.188
8631 | 23.186
8632 | 23.183
8633 | 23.183
8634 | 23.179
8635 | 23.175
8636 | 23.174
8637 | 23.173
8638 | 23.173
8639 | 23.167
8640 | 23.157
8641 | 23.156
8642 | 23.151
8643 | 23.149
8644 | 23.147
8645 | 23.142
8646 | 23.136
8647 | 23.133
8648 | 23.132
8649 | 23.132
8650 | 23.13
8651 | 23.13
8652 | 23.126
8653 | 23.122
8654 | 23.099
8655 | 23.095
8656 | 23.095
8657 | 23.08
8658 | 23.068
8659 | 23.065
8660 | 23.056
8661 | 23.053
8662 | 23.052
8663 | 23.051
8664 | 23.048
8665 | 23.045
8666 | 23.037
8667 | 23.034
8668 | 23.021
8669 | 23.016
8670 | 23.009
8671 | 23.009
8672 | 23.004
8673 | 22.997
8674 | 22.992
8675 | 22.991
8676 | 22.99
8677 | 22.972
8678 | 22.954
8679 | 22.948
8680 | 22.946
8681 | 22.937
8682 | 22.921
8683 | 22.914
8684 | 22.903
8685 | 22.901
8686 | 22.899
8687 | 22.891
8688 | 22.887
8689 | 22.881
8690 | 22.871
8691 | 22.864
8692 | 22.859
8693 | 22.856
8694 | 22.841
8695 | 22.834
8696 | 22.824
8697 | 22.824
8698 | 22.824
8699 | 22.824
8700 | 22.824
8701 | 22.824
8702 | 22.819
8703 | 22.8
8704 | 22.788
8705 | 22.783
8706 | 22.782
8707 | 22.78
8708 | 22.777
8709 | 22.772
8710 | 22.757
8711 | 22.73
8712 | 22.726
8713 | 22.719
8714 | 22.713
8715 | 22.698
8716 | 22.695
8717 | 22.693
8718 | 22.665
8719 | 22.661
8720 | 22.643
8721 | 22.639
8722 | 22.637
8723 | 22.598
8724 | 22.574
8725 | 22.548
8726 | 22.542
8727 | 22.542
8728 | 22.532
8729 | 22.518
8730 | 22.507
8731 | 22.506
8732 | 22.491
8733 | 22.485
8734 | 22.476
8735 | 22.473
8736 | 22.468
8737 | 22.419
8738 | 22.417
8739 | 22.415
8740 | 22.405
8741 | 22.373
8742 | 22.372
8743 | 22.36
8744 | 22.345
8745 | 22.336
8746 | 22.32
8747 | 22.303
8748 | 22.296
8749 | 22.278
8750 | 22.255
8751 | 22.234
8752 | 22.231
8753 | 22.179
8754 | 22.137
8755 | 22.06
8756 | 22.02
8757 | 21.952
8758 | 21.917
8759 | 21.892
8760 | 21.749
Insert

## Raw_Fuel_Data
References
| Fuel Costs: | http://www.eia.gov/oiaf/aeo/tablebrowser/#release=AEO2012&subject=3-AEO2012&table=3-AEO2012&region=1-0&cases=hccst12-d031312a,lccst12-d031312a,lm2012-d022412a,hm2012-d022412a,ref2012-d020112c
| except U238: | Assuming 33% thermal efficiency with 2010 fuel costs from: Energy Information Administration (EIA). (2013). Electric Power Annual 2011. Retrieved from http://www.eia.gov/electricity/annual/
| CO2: | EIA Voluntary Reporting of Greenhouse Gases Program: http://www.eia.doe.gov/oiaf/1605/coefficients.html
TX = West South Central Region in AEO
(for GAMS)
* | [name] | [t/MMBTU] | Fuel Cost [2010$/MMBTU]
| name | co2 | 2007 Historic-TX (PhD) | 2020 AEO2012-Ref-TX | 2030 AEO2012-Ref-TX | 2030 AEO2012-HiOilPrice-TX | 2030 AEO2012-LoOilPrice-TX | 2030 AEO2012-HiGrowth-TX | 2030 AEO2012-LoGrowth-TX | 2030 AEO2012-LoNuke-TX | 2030 AEO2012-HiNuke-TX | 2030 AEO2012-LoCoalCost-TX | 2030 AEO2012-HiCoalCost-TX | 2030 AEO2012-DemTech2011-TX | 2030 AEO2012-HiDemTech-TX | 2030 AEO2012-BestBuilding-TX | 2030 AEO2012-HiUltRecover-TX | 2030 AEO2012-LoUltRecover-TX | 2030 AEO2012-HiTechRecover-TX | 2030 AEO2012-LoFrozTech-TX | 2030 AEO2012-HighTech-TX | 2030 AEO2012-LowRenewCost-TX | 2030 AEO2012-ExtdPolicy-TX | 2030 AEO2012-NoSunset-TX | 2030 AEO2012-NgHdvPotnl-TX | 2030 AEO2013ER-Ref-TX | 2030 AEO2012-Ref-USA | 2030 AEO2012-HiGrowth-USA | 2030 AEO2012-LoGrowth-USA | 2030 AEO2012-LoCoalCost-USA | 2030 AEO2012-HiCoalCost-USA | 2030 AEO2012-HiUltRecover-USA | 2030 AEO2012-LoUltRecover-USA | 2030 AEO2012-HiTechRecover-USA | 2030 AEO2012-HighTech-USA | 2030 AEO2012-LoRenewCost-USA | 2035 AEO2012-Ref-TX | 2035 AEO2012-HiOilPrice-TX | 2035 AEO2012-LoOilPrice-TX | 2035 AEO2012-HiGrowth-TX | 2035 AEO2012-LoGrowth-TX | 2035 AEO2012-LoNuke-TX | 2035 AEO2012-HiNuke-TX | 2035 AEO2012-LoCoalCost-TX | 2035 AEO2012-HiCoalCost-TX | 2035 AEO2012-DemTech2011-TX | 2035 AEO2012-HiDemTech-TX | 2035 AEO2012-BestBuilding-TX | 2035 AEO2012-HiUltRecover-TX | 2035 AEO2012-LoUltRecover-TX | 2035 AEO2012-HiTechRecover-TX | 2035 AEO2012-LoFrozTech-TX | 2035 AEO2012-HighTech-TX | 2035 AEO2012-LowRenewCost-TX | 2035 AEO2012-ExtdPolicy-TX | 2035 AEO2012-NoSunset-TX | 2035 AEO2012-NgHdvPotnl-TX | 2035 AEO2013ER-Ref-TX | 2035 AEO2012-Ref-USA | 2035 AEO2012-HiGrowth-USA | 2035 AEO2012-LoGrowth-USA | 2035 AEO2012-LoCoalCost-USA | 2035 AEO2012-HiCoalCost-USA | 2035 AEO2012-HiUltRecover-USA | 2035 AEO2012-LoUltRecover-USA | 2035 AEO2012-HiTechRecover-USA | 2035 AEO2012-HighTech-USA | 2035 AEO2012-LoRenewCost-USA | Insert Spacer
u235 | u235 | 0 | 0.766 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605 | 0.64605
oil_dist | oil_dist | 0.07315 | NA | 24.725 | 27.091 | 34.933 | 13.599 | 27.772 | 25.861 | 26.806 | 26.849 | 27.086 | 26.963 | 27.002 | 25.935 | 26.935 | 26.35 | 27.501 | 24.959 | 27.108 | 25.695 | 26.396 | 25.42 | 26.686 | 24.451 | 27.304 | 26.43 | 27.23 | 25.32 | 26.51 | 26.43 | 25.73 | 26.95 | 24.42 | 25.17 | 25.86 | 28.48 | 35.518 | 14.217 | 29.66 | 27.712 | 28.725 | 28.104 | 28.652 | 28.716 | 28.681 | 28.038 | 28.482 | 27.882 | 28.975 | 26.581 | 29.029 | 2.599 | 28.486 | 26.407 | 28.75 | 26.58 | 29.729 | 27.8 | 29.02 | 27.17 | 27.94 | 28 | 27.27 | 28.38 | 26.01 | 26.87 | 27.8
oil_resid | oil_resid | 0.0788 | NA | 25.852 | 26.967 | 35.964 | 15.081 | 26.985 | 25.97 | 26.723 | 26.881 | 27.023 | 26.788 | 27.38 | 26.245 | 26.963 | 26.548 | 27.43 | 25.609 | 27.298 | 25.853 | 25.805 | 25.616 | 26.574 | 26.021 | 26.33 | 25.55 | 25.66 | 24.91 | 25.9 | 25.54 | 25.06 | 26.12 | 24.21 | 24.66 | 24.83 | 26.878 | 35.797 | 15.11 | 27.741 | 26.289 | 27.175 | 26.624 | 27.357 | 27.076 | 28.204 | 26.712 | 27.113 | 26.499 | 27.43 | 26.227 | 28.348 | 26.155 | 26.812 | 25.934 | 27.348 | 26.684 | 28.53 | 25.72 | 26.49 | 25.25 | 26.11 | 25.87 | 25.17 | 26.45 | 24.95 | 25.13 | 25.69
ng | ng | 0.05306 | 6.84 | 4.353 | 5.784 | 5.794 | 5.862 | 6.338 | 5.207 | 5.881 | 5.683 | 5.585 | 6.279 | 6.187 | 4.986 | 4.488 | 4.914 | 7.216 | 3.773 | 6.213 | 4.852 | 5.467 | 5.289 | 5.543 | 6.163 | 5.552 | 6.21 | 6.77 | 5.61 | 5.99 | 6.71 | 5.36 | 7.62 | 4.1 | 5.23 | 5.86 | 6.766 | 6.524 | 6.71 | 7.064 | 6.076 | 7.467 | 6.606 | 6.337 | 7.265 | 7.3 | 5.729 | 5.143 | 5.511 | 7.655 | 4.214 | 7.416 | 5.323 | 6.153 | 5.893 | 6.288 | 7.415 | 6.426 | 7.21 | 7.4 | 6.55 | 6.78 | 7.72 | 6.03 | 7.94 | 4.51 | 5.69 | 6.61
coal | coal | 0.09552 | 1.956 | 2.119 | 2.493 | 2.685 | 2.261 | 2.55 | 2.45 | 2.495 | 2.491 | 1.708 | 3.697 | 2.535 | 2.4 | 2.297 | 2.439 | 2.54 | 2.303 | 2.518 | 2.366 | 2.472 | 2.441 | 2.485 | 2.478 | 2.544 | 2.66 | 2.73 | 2.62 | 1.85 | 4.04 | 2.6 | 2.73 | 2.46 | 2.54 | 2.64 | 2.636 | 2.856 | 2.369 | 2.683 | 2.578 | 2.643 | 2.625 | 1.626 | 4.422 | 2.695 | 2.531 | 2.405 | 2.58 | 2.671 | 2.414 | 2.687 | 2.483 | 2.613 | 2.54 | 2.615 | 2.599 | 2.716 | 2.8 | 2.87 | 2.75 | 1.77 | 4.79 | 2.73 | 2.86 | 2.57 | 2.65 | 2.77
coal_anth | coal_anth | 0.10369 | 1.956 | 2.119 | 2.493 | 2.685 | 2.261 | 2.55 | 2.45 | 2.495 | 2.491 | 1.708 | 3.697 | 2.535 | 2.4 | 2.297 | 2.439 | 2.54 | 2.303 | 2.518 | 2.366 | 2.472 | 2.441 | 2.485 | 2.478 | 2.544 | 2.66 | 2.73 | 2.62 | 1.85 | 4.04 | 2.6 | 2.73 | 2.46 | 2.54 | 2.64 | 2.636 | 2.856 | 2.369 | 2.683 | 2.578 | 2.643 | 2.625 | 1.626 | 4.422 | 2.695 | 2.531 | 2.405 | 2.58 | 2.671 | 2.414 | 2.687 | 2.483 | 2.613 | 2.54 | 2.615 | 2.599 | 2.716 | 2.8 | 2.87 | 2.75 | 1.77 | 4.79 | 2.73 | 2.86 | 2.57 | 2.65 | 2.77
coal_bit | coal_bit | 0.09328 | 1.956 | 2.119 | 2.493 | 2.685 | 2.261 | 2.55 | 2.45 | 2.495 | 2.491 | 1.708 | 3.697 | 2.535 | 2.4 | 2.297 | 2.439 | 2.54 | 2.303 | 2.518 | 2.366 | 2.472 | 2.441 | 2.485 | 2.478 | 2.544 | 2.66 | 2.73 | 2.62 | 1.85 | 4.04 | 2.6 | 2.73 | 2.46 | 2.54 | 2.64 | 2.636 | 2.856 | 2.369 | 2.683 | 2.578 | 2.643 | 2.625 | 1.626 | 4.422 | 2.695 | 2.531 | 2.405 | 2.58 | 2.671 | 2.414 | 2.687 | 2.483 | 2.613 | 2.54 | 2.615 | 2.599 | 2.716 | 2.8 | 2.87 | 2.75 | 1.77 | 4.79 | 2.73 | 2.86 | 2.57 | 2.65 | 2.77
coal_sub | coal_sub | 0.09717 | 1.956 | 2.119 | 2.493 | 2.685 | 2.261 | 2.55 | 2.45 | 2.495 | 2.491 | 1.708 | 3.697 | 2.535 | 2.4 | 2.297 | 2.439 | 2.54 | 2.303 | 2.518 | 2.366 | 2.472 | 2.441 | 2.485 | 2.478 | 2.544 | 2.66 | 2.73 | 2.62 | 1.85 | 4.04 | 2.6 | 2.73 | 2.46 | 2.54 | 2.64 | 2.636 | 2.856 | 2.369 | 2.683 | 2.578 | 2.643 | 2.625 | 1.626 | 4.422 | 2.695 | 2.531 | 2.405 | 2.58 | 2.671 | 2.414 | 2.687 | 2.483 | 2.613 | 2.54 | 2.615 | 2.599 | 2.716 | 2.8 | 2.87 | 2.75 | 1.77 | 4.79 | 2.73 | 2.86 | 2.57 | 2.65 | 2.77
coal_lig | coal_lig | 0.09772 | 1.956 | 2.119 | 2.493 | 2.685 | 2.261 | 2.55 | 2.45 | 2.495 | 2.491 | 1.708 | 3.697 | 2.535 | 2.4 | 2.297 | 2.439 | 2.54 | 2.303 | 2.518 | 2.366 | 2.472 | 2.441 | 2.485 | 2.478 | 2.544 | 2.66 | 2.73 | 2.62 | 1.85 | 4.04 | 2.6 | 2.73 | 2.46 | 2.54 | 2.64 | 2.636 | 2.856 | 2.369 | 2.683 | 2.578 | 2.643 | 2.625 | 1.626 | 4.422 | 2.695 | 2.531 | 2.405 | 2.58 | 2.671 | 2.414 | 2.687 | 2.483 | 2.613 | 2.54 | 2.615 | 2.599 | 2.716 | 2.8 | 2.87 | 2.75 | 1.77 | 4.79 | 2.73 | 2.86 | 2.57 | 2.65 | 2.77
wind | wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
water | water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(for GAMS) | Insert Spacer
Note on D10: Bryan Palmintier: Used for PhD Thesis in thesis_fuels.inc

## References
Data Source(s):
OLD OLD OLD
Generator Costs
*
* with life estimates based on:
* Royal Academy of Engineering. (2004). The cost of generating electricity.
* London: Royal Academy of Engineering.
*
* Technology Mapping:
* DOE AEO2010
* Nuke Advanced Nuclear
* Coal Scrubbed Coal, New
* CCGT Adv Gas/Oil Comb Cycle
* CT Adv Comb Turbine
* Wind Wind
*
* Notes & Assumptions:
* - Capital Costs are Total Overnight costs
* - Costs in 2006 $'s
Fuel Costs
EIA AOE2010 Table 3, Electricity Sector fuel prices for 2030
* except u235 based on:
* Royal Academy of Engineering. (2004). The cost of generating electricity.
* London: Royal Academy of Engineering.
* for fuel prices and heatrate from:
* EIA Annual Energy Outlook, 2010 Table 8.2 Generator Cost Assumptions
Carbon Values
* co2: EIA Voluntary Reporting of Greenhouse Gases Program:
* http://www.eia.doe.gov/oiaf/1605/coefficients.html
* ng: pipeline natural gas
* coal: subbituminos
Availability & Capacity Factors
Estimates
Load Data
ERCOT historic hourly load data for 2009
supplied by ERCOT via Mort Webster