## Sheet1
name | c_var_om | c_fix_om | c_cap | life | fuel | heatrate | c_fuel | Development |  | Early Construction |  | Commited Construction |  | lead_time | co2_embed | co2_ccs | p_min | maintenance_days | forced_out | repair_time | avg_avail | cap_credit | plant_size | ramp_max | min_percent | unit_min | c_start_fix | fuel_start | min_up | min_down | quick_start | reg_up | reg_down | spin_rsv | max_start
| $/MWh | $/MW-yr | $/MW | yr |  | kBTU/MWh | $/MWh | yr | cost% | yr | cost % | yr | cost% |  |  |  |  | day/yr |  | hr | [8 empty] | hr | hr
currently used by Adv Power Tools (including IEEE 2011 paper)
Nuke | 0.51 | 92040 | 3820000 | 40 | u235 | 10.488 | [7 empty] | 6 | 0 | 0 | 0 |  |  |  |  | 0.9 | 1350 | 0.01 |  | 1250 | 100000 | 10000 |  |  | 0 | 0 | 0 | 0 | 2
Coal | 4.69 | 28150 | 2223000 | 30 | coal | 9.2 | [7 empty] | 4 | 0 | 0 | 0 |  |  |  |  | 0.85 | 600 | 0.1 |  | 300 | 20000 | 10000 |  |  | 0 | 0.002 | 0.002 | 0.017 | 50
CCGT | 2.04 | 11960 | 968000 | 30 | ng | 6.752 | [7 empty] | 3 | 0 | 0 | 0 |  |  |  |  | 0.85 | 400 | 0.8 |  | 150 | 5000 | 1000 |  |  | 0 | 0.025 | 0.025 | 0.25 | 300
CT | 3.24 | 10770 | 648000 | 20 | ng | 9.289 | [7 empty] | 2 | 0 | 0 | 0 |  |  |  |  | 0.85 | 230 | 6 |  | 10 | 100 | 0 |  |  | 1 | 0.05 | 0.05 | 0.5 | Inf
Wind | 0 | 30980 | 1966000 | 20 | wind | 1 | [7 empty] | 3 | 0 | 0 | 0 |  |  |  |  | 0.1 | 50 | 1 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | Inf
from de Jonghe, et al 2011 (** Costs in Euros) - ?? Cap costs annualized?
Base (nuke) | 5 | 65000 | 155000 |  |  |  | 10 | [16 empty] | 0.33
Mid (coal) | 10 | 35000 | 65000 |  |  |  | 20 | [16 empty] | 0.5
Peak (CCGT) | 10 | 15000 | 25000 |  |  |  | 35 | [16 empty] | 0.8
High Peak (CT/Oil) | 10 | 10000 | 15000 |  |  |  | 65 | [16 empty] | 1
Sixth NW Conservation & Power Plan |  | $/kW/yr + tax & insurance | $2006/kW overnight |  |  | BTU/kWh | [16 empty] | net
Coal Steam-wet (supercritical) | 2.75 | 60 | 3500 | 30 | coal | 9000 |  | 3 | 3% | 1 | 11% | 3 | 86% | 4 |  |  |  | 35 | 7% | 40 | 0.85 | 93% | 450 | 0.3 | 50% | 225 |  |  | 24 | 12 |  | 0.006 | 0.006 | 0.05
Coal Steam-dry | [5 empty] | 10% lower (effect 3x larger than CCGT)
Coal+CCS Steam-wet (supercritical) | 5.86 | 128 | 5635 | 30 | coal | 11880 |  | 3 | 3% | 1 | 11% | 3 | 86% | 4 |  | 0.9 |  | 35 | 7% | 40 | 0.85 | 93% | 450 | 0.3 | 50% | 225 |  |  | 24 | 12 |  | 0.006 | 0.006 | 0.05
IGCC | 6.3 | 45 | 3600 | 30 | coal | 8680 |  | 3 | 2% | 1 | 31% | 3 | 67% | 4 |  |  |  | 30 | 10% | unknown | 0.81 | 90% | 623 | 0.1 | 70% | 436.1 |  |  | 120 | 24 |  | 0.002 | 0.002 | 0.016667
IGCC+CCS | 8.5 | 60 | 4800 | 30 | coal | 10760 |  | 3 | 2% | 1 | 31% | 3 | 67% | 4 |  | 0.88 |  | 30 | 10% |  | 0.81 | 90% | 518 | 0.1 | 70% | 362.6 |  |  | 120 | 24 |  | 0.002 | 0.002 | 0.016667
NG-CT-Aero derivative | 4 | 13 | 1050 | 30 | ng | 9370 |  | 1.5 | 5% | 0.75 | 50% | 0.5 | 45% | 1.25 |  |  |  | 14 | 5% | 88 | 0.91 | 95% | 92 | 6 | 25% | 23 |  |  | 1 | 1 |  | 0.12 | 0.12 | 1
NG-CT-Frame | 1 | 11 | 610 | 30 | ng | 11870 |  | 1.5 | 5% | 0.75 | 50% | 0.5 | 45% | 1.25 |  |  |  | 14 | 5% | 88 | 0.91 | 95% | 81 | 6 | 25% | 20.25 |  |  | 1 | 1 |  | 0.12 | 0.12 | 1
NG-CT-Intercool
NG-Reciprocate
NG-CCGT | 1.7 | 14 | 1120 | 30 | ng | 6930 |  | 2 | 4% | 1 | 42% | 1.5 | 54% | 2.5 |  |  |  | 21 | 6% | 32 | 0.89 | 1.001 | 385 | 1 | 70% | 269.5 |  |  | 6 | 12 |  | 0.02 | 0.02 | 0.16667
Nuke | 1 | 90 | 5500 | 30-60 | u235 | 10400 |  | 4 | 5% | 2 | 30% | 4 | 65% | 6 |  |  |  | 28 | 4.2% | 112 | 0.9 | 95.8% | 1117 | 0.1 | 70% | 781.9 |  |  | 120 | 24 |  | 0.002 | 0.002 | 0.016667
Wind | 2 | 40 | 2100 | 20 | wind | 1 |  | 2 | 5% | 1 | 16% | 1.5 | 79% | 2.5 | [7 empty] | 0.05 | 100
Solar-utility-PV
Solar-concentrating
Hydro
Geothermal
Power Globe Post by Mike Adibi, October 06, 2011
Coal & Oil Steam | [25 empty] | 30%
Nuclear | [25 empty] | 25%
Gas Turbine | [25 empty] | 10%
Combined Cycle & Hydro | [25 empty] | 5-10%
Note on A19: Bryan Palmintier: Note: data for IGCC has many assumptions ex: reliability data from nukes
Note on W25: Bryan Palmintier: >1 b/c of 25MW supplimental capacity